## Getting Started
Version 3.5, October 2023
Go to the
Input Screen
Go to the
Input Screen
Go to the
Input Screen
Go to the
Input Screen
CONTACT US
We welcome your input on the calculator’s usability and functionality. Should you encounter any bugs when using the calculator, or if you have questions about how to use the calculator, please contact the EPA CHP Partnership at chp@epa.gov or 703-373-8108.
The calculator was originally developed by the U.S. Department of Energy's Distributed Energy Program and Oak Ridge National Laboratory. Modifications and enhancements have been subsequently made by ICF on behalf of the EPA CHP Partnership.
INTRODUCTION AND PURPOSE
The calculator is a Microsoft Excel-based tool that estimates the energy and emissions savings of a CHP system by comparing the estimated energy use and air pollutant emissions (CO2e, SO2 and NOX) of a CHP system and the estimated energy use and emissions associated with the same quantity of grid-supplied power and output from an on-site boiler system.
The calculator is designed for users with at least a moderate understanding of CHP technology and its terminology. The User Manual, the document attached at the top of this page, provides detailed instructions on how to use this tool. For more information about CHP technologies, benefits, emissions calculation methodology, and why EPA supports CHP, please visit www.epa.gov/chp.
Please note that the results generated by the calculator are intended for educational and outreach purposes only and are not intended for use in developing emissions inventories or preparing air permit applications. The accuracy of the results is a function of the accuracy and completeness of the user inputs.
BASIC DIRECTIONS FOR USE
The primary components of the calculator are the Inputs and Results Worksheets:
Inputs Worksheet
The Inputs Worksheet consists of 32 input fields that are used to characterize the CHP system being evaluated and comparable displaced electricity and thermal production. Note that some inputs are not applicable to every CHP or displaced electricity and thermal production system and therefore do not need to be completed.
Enter Inputs 1 through 6 at a minimum. Default values can be optionally selected for inputs 7 through 25. Please note that the accuracy of the calculator’s results is improved by completing as many inputs as possible with system-specific information. Values (other than default values) must be entered for inputs 1 through 25 for the most accurate estimates of energy savings. In addition, inputs 26 through 32 must be entered to estimate emissions savings.
Each Input field has three components: a question, at least one input cell, and a 'Submit' button. To complete an input, choose one of these three options:
1) Manually enter or select (from a pull-down menu) system-specific information.
2) Use default system information provided (in certain cases) in the available Microsoft Excel note.
  The calculator information for certain inputs in the form of Excel notes. To view the notes, move the cursor over red triangle in the upper right-hand corner of the cell.
3) Skip the input.
After completing an input, click on the 'Submit' button, which moves the cursor to the next appropriate input field.
Once all inputs are completed, click on one of the 'Check All Inputs and Go to Results' buttons on the Inputs Worksheet. This action will either open the Results Worksheet or display an error message numbers of the Inputs numbers that need attention.
Example:
Results Worksheet
The Results Worksheet includes several tables:
- Table 1: Annual Energy Savings—presents the energy consumption of the CHP and the displaced electricity and thermal production, the total energy savings from using CHP, and CHP energy savings expressed in terms of the annual energy use of passenger cars and annual electricity use in homes.
- Table 2: Annual Emissions Savings—presents the emissions associated with CHP and displaced electricity and thermal production systems and the emissions savings by using CHP. It also presents the CHP GHG savings in terms of the emissions associated with passenger vehicles and the generation of electricity used by the average U.S. home.
- Table 3: CHP Technology and Generation Profile—presents a summary of CHP information.
- Table 4: Displaced Thermal Energy—presents information about displaced thermal production (i.e., the amount of energy required to produce thermal energy in the displaced electricity and thermal production system).
- Table 5: Displaced Electricity—presents information about the displaced electric production (i.e., the amount of energy required to produce electricity in the displaced electricity and thermal production).
Note: If only energy savings associated with CHP are estimated (i.e., only inputs 1 through 25 on the Inputs Worksheet are completed), Tables 1 through 5 only will appear on the Results Worksheet (however, in this case Table 2 will not display data). If all inputs (1 through 32) are estimated, Tables 1 through 10 will appear with displayed data.
- Table 6: Annual Analysis for CHP—presents the annual energy use and emissions from the CHP system.
- Table 7: Annual Analysis for Displaced Thermal Production (non-cooling)–-presents the annual energy use and emissions associated with displaced thermal production.
- Table 8: Annual Analysis for Displaced Electricity Production—presents the annual energy use and emissions associated with displaced electricity production.
- Table 9: Emission Rates for Displaced Electricity—presents the emissions rates by pollutant for CHP and displaced electricity.
- Table 10: Emission Rates for Displaced Thermal—presents the emission rates by pollutant associated with the displaced thermal production.
In addition to the tables, two schematic flow diagrams appear on the Results Worksheet. If users estimate only energy savings, the diagrams show the energy input and output flows associated with displaced electricity and thermal production and CHP. If the user also estimates emissions savings, the diagrams show the emissions associated with displaced electricity and thermal production and CHP, in addition to the energy use.
CONTACT US
We welcome your input on the calculator’s usability and functionality. Should you encounter any bugs when using the calculator, or if you have questions about how to use the calculator, please contact the EPA CHP Partnership at chp@epa.gov or 703-373-8108.
The calculator was originally developed by the U.S. Department of Energy's Distributed Energy Program and Oak Ridge National Laboratory. Modifications and enhancements have been subsequently made by the EPA CHP Partnership.
Go to the
Input Screen

## Inputs
|  |  | 0 | 0 | 0
Energy Savings Inputs
CHP System Characteristics
1. CHP: Type of System | 0
1
2. CHP: Electricity Generating Capacity (per unit)
| 0 | kW |  |  | 0
0
0
3. CHP: How Many Identical Units (i.e., engines) Does This System Have? |  |  |  |  | 0
| 1 |  |  |  | 0
0
0
4. CHP: Annual Utilization (Enter a value to answer only ONE of the options below) |  |  |  |  | 0
Option 1: How many hours per year does the CHP system operate? |  |  |  |  | 0
| 0 |  |  |  | 0
0
As a number of hours per year | 0 |  |  |  | 0
OR As a percentage | 0% |  |  |  | 0
0
Option 2: How much grid electricity is displaced by CHP operation each year? |  |  |  |  | 0
Enter displaced grid electricity as MWh/year | 0 | MWh/yr |  |  | 0
0
0
5. CHP: Does the System Provide Heating or Cooling or Both? |  |  |  |  | 0
| 0 |  |  |  | 0
0
If Heating and Cooling: How many of the hours are in cooling mode? |  |  |  |  | 0
0
As a number of hours per year | 0 |  |  |  | 0
as a percentage of the hours? | 0% |  |  |  | 0
0
If Heating and Cooling: Does the System Provide Simultaneous Heating and Cooling? |  |  |  |  | 0
| 0 |  |  |  | 0
0
0
6. CHP: Fuel |  |  |  |  | 0
Fuel Type | 0 |  |  |  | 0
0
0
0
7. CHP: What is the Heat Content of this Fuel? (Enter a value in only ONE of the boxes) |  |  |  |  | 0
| 0 | Btu/cubic foot (HHV) |  |  | 0
OR | 0 | Btu/gallon (HHV) |  |  | 0
OR | 0 | Btu/lb (HHV) |  |  | 0
0
0
8. CHP: Boiler Steam To Process (Steam Turbine CHP Only) |  |  |  |  | 0
0
Boiler Steam to Process as lb Steam/hr | 0 |  |  |  | 0
Boiler Steam to Process as MMBtu Steam/hr | 0 |  |  |  | 0
0
0
9. CHP: Steam Turbine System Boiler Efficiency (Steam Turbine CHP Only) |  |  |  |  | 0
0
0
Enter Boiler Efficiency as % | 0% |  |  |  | 0
0
0
10. CHP: Electric Efficiency |  |  |  |  | 0
0
0 |  |  |  |  | 0
Enter Generating Efficiency as % | 0% | (HHV) |  |  | 0
OR Enter Generating Efficiency as Btu/kWh HHV | 0 | Btu/kWh (HHV) |  |  | 0
OR Enter Generating Efficiency as Btu/kWh LHV | 0 | Btu/kWh (LHV) |  |  | 0
0
0
11. CHP Equipment: Base Power to Heat Ratio |  |  |  |  | 0
The Power to Heat Ratio should reflect ONLY the thermal production of the generating unit (i.e., combustion turbine). |  |  |  |  | 0
Thermal Output of the duct burners (if equipped) should not be included. |  |  |  |  | 0
0
| See the SubThermalCalculator for help on calculating a Power to Heat Ratio |  |  |  | 0
Power to Heat Ratio (Generating Unit Capacity) | 0 |  |  |  | 0
If WHP: Useful Thermal Output (MMBtu/hr) | 0 |  |  |  | 0
0
0
12. Duct Burners: Does the System Incorporate Duct Burners? (Duct Burners only allowed on Combustion Turbines) |  |  |  |  | 0
0 | 0 |  |  |  | 0
0
0
13. Duct Burners: What is the Total Fuel Input Capacity of the Burners for Each CHP Unit? |  |  |  |  | 0
0
| 0 | MMBtu/hr |  |  | 0
0
0
14. Duct Burners: The CHP system operates hours per year. How much do the Duct Burners operate? |  |  |  |  | 0
As a number of hours per year | 0 |  |  |  | 0
As a percentage of the hours? | 0% | 0 |  |  | 0
0
CHP Cooling Characteristics |  |  |  |  | 0
0
15. Cooling: Does the CHP Provide Cooling? | No |  |  |  | 0
2 | You indicated No Cooling in Item 5 |  |  |  | 0
0
16. Cooling: What is the Coefficient of Performance (COP) of the Absorption Chiller Used? |  |  |  |  | 0
| 0 | 0 |  |  | 0
0
Coefficient of Performance (COP) | 0 |  |  |  | 0
0
0
17. Cooling: What is the Cooling Capacity of the System? |  | 0 |  |  | 0
0
0
(Enter a value in only ONE of the boxes) | 0 | Cooling Tons |  |  | 0
| 0 | OR MMBtu per Hour of Cooling |  |  | 0
0
0
18. Displaced Cooling: What is the Efficiency of the Cooling System that is Being Displaced? |  |  |  |  | 0
| 0 |  |  |  | 0
|  | 0 |  |  | 0
(Enter a value in only ONE of the boxes) |  |  |  |  | 0
Electricity Demand (kW per ton) | 0 |  |  |  | 0
OR Coefficient of Performance (COP) | 0 |  |  |  | 0
0
Thermal Characteristics |  |  |  |  | 0
0
19. Displaced Thermal: Type of System: | 0 |  |  |  | 0
0
0
20. Displaced Thermal: What is the Heat Content of the displaced Fuel? (Enter a value in only ONE of the boxes) |  |  |  |  | 0
| 0 | Btu/cubic foot (HHV) |  |  | 0
OR | 0 | Btu/gallon (HHV) |  |  | 0
OR | 0 | Btu/lb (HHV) |  |  | 0
0
0
21. Displaced Thermal: Efficiency (usually a boiler) |  |  |  |  | 0
0
Enter Generating Efficiency as % | 0% |  |  |  | 0
0
0
22. Thermal Utilization (Enter a value to answer only ONE of the options below) |  |  |  |  | 0
Option 1: CHP Thermal Utilization - What is the percent of available CHP thermal output utilized throughout the year? |  |  |  |  | 0
0
Enter thermal utilization as a % | 0% |  |  |  | 0
(also applies to cooling) |  |  |  |  | 0
Option 2: Displaced boiler fuel - What is the quantity of boiler fuel displaced throughout the year? |  |  |  |  | 0
Enter displaced boiler fuel as MMBtu/year | 0 | MMBtu/yr |  |  | 0
0
Electricity Profile |  |  |  |  | 0
0
23. Displaced Electricity: Electricity Generation Profile |  |  |  |  | 0
| 1 |  |  |  | 0
See the instructions for Input 23 in Section 2 of the User Manual |  |  |  | If Range("deinput") = 14 | If Range("deinput") = 14
0
0
24. Displaced Electricity: Select U.S. Average, eGRID Subregion, NERC region, or AVERT region |  |  |  |  | 0
| 1 |  |  |  | 0
Link to eGRID Subregion Map, NERC Interconnections Map, and AVERT Region Map |  |  | *Stop entering inputs here to calculate ONLY energy savings - continue entering inputs to calculate energy AND emissions savings |  | 0
0
0
25. Displaced Electricity: Select Electric Grid Region for Transmission and Distribution (T&D) Losses |  |  |  |  | 0
AVERT regions already have grid loss included in emission factors, so default is set to zero | 0 |  |  |  | 0
0
Link to NERC Interconnections Map |  |  |  |  | 0
0
Emissions Savings Inputs |  |  |  |  | 0
CHP & Displaced Boiler Emissions Characteristics |  |  |  |  | 0
0
26. CHP: If Biomass, Diesel, Distillate, Coal or Other: What is the Sulfur Content? |  |  |  |  | 0
If WHP, what is the sulfur content of the stack? |  |  |  |  | 0
| or |  |  |  | 0
0 |  |  |  |  | 0
0
Enter Sulfur Content of Fuel as a percent | 0% |  |  |  | 0
OR ppm | 0 | ppm |  |  | 0
0
0
27. CHP: What is the CO2 Emission Rate for this Fuel? (default completed for fuel in Item 6) |  |  |  |  | 0
Enter alternative value: | 0 | lb CO2/MMBtu |  |  | 0
0
0
28. CHP: NOx Emission Rate |  |  |  |  | 0
0
0 | 2 |  |  |  | 0
0
Enter a NOx Rate as ppm (15% O2) | 0 | ppm |  |  | 0
OR Enter a NOx Rate as gm/hp-hr | 0 | gm/hp-hr |  |  | 0
OR Enter a NOx Rate as lb/MMBtu | 0 | lb NOx/MMBtu |  |  | 0
OR Enter a NOx Rate as lb/MWh | 0 | lb NOx/MWh |  |  | 0
0
0
29. Duct Burners: NOx Emission Rate for the Duct Burners |  |  |  |  | 0
| 2 |  |  |  | 0
0 |  |  |  |  | 0
0 | 0 | lb/MMBtu |  |  | 0
OR | 0 | ppm NOx at 15% O2 |  |  | 0
0
0
30. Displaced Thermal: What is the CO2 Emission Rate for this Fuel? |  |  |  |  | 0
Enter alternative value: | 0 | lb CO2/MMBtu |  |  | 0
0
0
31. Displaced Thermal: If Biomass, Diesel, Distillate, Coal or Other: What is the Sulfur Content? |  |  |  |  | 0
| 1 |  |  |  | 0
| or |  |  |  | 0
0
0 |  |  |  |  | 0
Enter Sulfur Content as a percent | 0% |  |  |  | 0
OR ppm | 0 | ppm |  |  | 0
0
0
32. Displaced Thermal Production: NOx Emission Rate |  |  |  |  | 0
0
NOx Rate | 0 | lb NOx/MMBtu |  |  | 0
0
CHP Fuel
#N/A | co2 flag
#N/A | heat content flag
Displaced Thermal Production Fuel
#N/A | so2 flag
#N/A | co2 flag
#N/A | heat content flag
Use default for this technology
I will enter a Power to Heat ratio
I will enter a value in one
of the following blocks
High sulfur oil: 0.15% or 1,500 ppm
Low sulfur oil: 0.05% or 500 ppm
Ultra low sulfur diesel: 15 ppm
I will enter an efficiency in one of the following blocks
Use default for this technology
I will enter a NOx rate in one
of the following blocks
Use default emissions for this technology.
Note: Default emissions are without aftertreatment. Some areas may require add-on controls and you will need to enter an emission rate based on your local requirements. SCR can reduce emissions by up to 90%
I will enter the NOx rate
Use default for NOx rate
I will enter a value
Commercial coal: 1% sulfur
High sulfur oil: 0.15% or 1,500 ppm
Low sulfur oil: 0.05% or 500 ppm
Reset All Inputs
Use the Thermal
Calculator to calculate
my Power to Heat Ratio
I will enter an efficiency
Use default for this thermal technology
I will enter a NOx rate in one
of the following blocks
Use default for this technology
Submit
Check All Inputs and Go to Results
Check All Inputs and Go to Results
Check All Inputs and Go to Results
Check All Inputs and Go to Results
Check All Inputs and Go to Results
Check All Inputs and Go to Results
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Check All Inputs and Go to Results
Submit
I will enter an efficiency
Submit
Use default for this technology
View biomass and coal fuel characteristics
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Modify one of the User-Defined Profiles
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
Submit
I will enter a thermal utilization
Use the default thermal utilization
Check All Inputs and Go to Results
Note on B9: Enter the size of the CHP system as measured in kilowatts (kW) of electricity production. If there are multiple units, enter the nameplate capacity for a single unit.
Note on B13: Enter the number of identical units in this CHP system. For many systems, there is only one unit. If there are multiple identical units, enter the number here. If the units are not identical, they must be analyzed separately.
Note on B20: Enter value for the number of hours per year that the CHP system operates. The total number of hours in a year is 8,760. The pull-down menu provides some typical operating schedules.
Note on B21: Enter value for the percentage of the year that the CHP system operates The total number of hours in the year is 8,760.
Note on B24: Enter value for the grid electricity displaced by CHP in MWh/year Must not be larger than CHP system capacity * 8,760 (hours in a year)
Note on B32: Enter value for the number of hours per year that the CHP system operates in cooling mode. The spreadsheet lists the number of hours for reference.
Note on B33: Enter value for the percentage of the year that the CHP system operates in cooling mode.
Note on B45: The heat content of gaseous fuels is usually described as Btu per cubic foot. Natural gas has a heat content of 1028 Btu/CF.
Note on B46: The heat content of liquid fuels is described as Btu per gallon. The average heat content for distillate oil or diesel fuel is 138,000 Btu/gallon The average heat content for residual oil is 150,000 Btu/gallon
Note on B47: The heat content of solid fuels is described in terms of Btu per pound. The average heat content of coal is between 7,000 and 12,000 Btu per pound. The average heat content of wood is between 4,000 and 8,500 Btu per pound depending on moisture content.
Note on B59: Enter value for efficiency of the boiler. The efficiency is the ratio of the useful thermal output divided by the fuel input. Typical boiler efficiencies are between 80% and 85%.
Note on B65: Enter value for electricity generating efficiency of the CHP unit. A percentage is most often used for engines. The generating efficiency is equal to the electricity produced divided by the fuel input. The units can be converted by using the general conversion of 3,412 Btu per kilowatt-hour
Note on B66: Enter value for the heat rate of the CHP unit. Higher Heating Value (HHV) heat rates are usually used with boilers. The heat rate is the amount of fuel input needed to produce 1 kWh of electricity. The fuel input is measured in Btu's on a Higher Heating Value (HHV) basis.
Note on B67: Enter value for the heat rate of the CHP unit. Lower Heating Value (LHV) Heat rates are usually used with turbines. The heat rate is the amount of fuel input needed to produce 1 kWh of electricity. The fuel input is measured in Btu's on a Lower Heating Value (LHV) basis.
Note on B75: Enter the Power to Heat ratio for the CHP system. Power is the electricity output and Heat is the useful thermal output. There are several methods for calculating the power to heat ratio and the "Thermal Calculator" may provide useful guidance.
Note on B85: Enter the Fuel Input Capacity of the Duct Burner(s) This value is the fuel supply rate to the duct burner(s) measured on a MMBtu per hour basis. For reference only, the spreadsheet lists the heat input rate of the CHP unit. The fuel input rate of the duct burner(s) may be higher or lower than that of the CHP unit. Generally the fuel input rate for the duct burner(s) is within 50% of the fuel input rate of the CHP unit. Duct burners provide supplemental heat to the exhaust downstream from the CHP unit. Combustion turbines are the most common system to use duct burners.
Note on B89: Enter value for the number of hours per year that the duct burner(s) operate. The spreadsheet lists the number of hours per year that the CHP system operates. The duct burners can operate the same or fewer hours than the CHP system but not more hours.
Note on B90: Enter the percentage of CHP operating hours that that duct burner(s) operate. The spreadsheet lists the number of hours per year that the CHP system operates.
Note on B100: Enter the Coefficent of Performace (COP) for the CHP cooling system. The COP is equal to the cooling delivered by the system divided by the thermal energy used by the chiller. COP=0.7 for a typical single-effect absorption chiller COP=1.4 for a typical double-effect absorption chiller
Note on B106: Enter the Cooling Capacity in Tons One Ton of Cooling equals 12,000 Btu per hour of cooling service. The spreadsheet lists the maximum cooling capacity that can be served based on the inputs that the user has given.
Note on B107: Enter the Cooling Capacity in MMBtu/hr of cooling service. The spreadsheet lists the maximum cooling capacity that can be served based on the inputs that the user has given.
Note on B114: Enter the kW per ton value for the efficiency of the cooling system that is being displaced. The "kW" represents the electrical demand for the cooling system. "Tons" represents the cooling capacity of the cooling system. One "ton" equals 12,000 Btu/hour of cooling capability. The pulldown menu lists a range of default systems with typical efficencies.
Note on B115: Enter the COP Value for the Displaced Cooling System. The COP is equal to the cooling delivered by the system divided by the thermal energy used by the chiller. The pulldown menu lists a range of default systems with typical efficencies.
Note on B119: Enter fuel used in boiler
Note on B123: The heat content of gaseous fuels is usually described as Btu per cubic foot. Natural gas has a heat content of 1028 Btu/CF.
Note on B124: The heat content of liquid fuels is described as Btu per gallon. The average heat content for distillate oil or diesel fuel is 138,000 Btu/gallon.
Note on B125: The heat content of solid fuels is described in terms of Btu per pound. The average heat content of coal is between 7,000 and 12,000 Btu per pound.
Note on B130: Enter value for efficiency of the displaced boiler. The efficiency is the ratio of the useful thermal output divided by the fuel input. Typical boiler efficiencies are between 80% and 85%. Electric Heat Pump efficiencies can exceed 100%.
Note on B136: Enter a thermal utilization for the CHP system between 0 and 100% If left blank, calculations will assume a default 80% thermal utilization
Note on B139: Enter the displaced boiler fuel in MMBtu/year. This cannot be larger than the calculated maximum amount of displaced fuel based on the CHP generation capacity (MWh).
Note on B155: Enter the transmission losses for the displaced electricity. This value represents the losses in the transmisson and distribution of electricity from the powerplant to the customer. The specific true value for transmission losses varies with location and time. The eGRID US average transmission loss value is 4.87%.
Note on B166: Enter value for sulfur content of oil. Sulfur contents above 1% are very unusual in units of this size. Information on fuels can be found at: http://eia.doe.gov/indexnjava.html
Note on B167: Enter value for sulfur content of oil. This entry represents the sulfur content as Parts Per Million (ppm). Information on fuels can be found at: http://eia.doe.gov/indexnjava.html
Note on B171: The CO2 emission rate for fuels is primarily based on the type of fuel. Typical values: Natural gas: 116.9 lb/MMBtu Oil: 163.1 lb/MMBtu Coal (Industrial - Mixed Use): 207.1 lb/MMBtu Propane: 139 lb/MMBtu The fuel-specific values come from EPA’s Mandatory Greenhouse Gas Reporting Rule. http://ecfr.gpoaccess.gov/cgi/t/text/textidx?c=ecfr&sid=69252b18e978de71ebe95c500dd9e47c&rgn=div9&view=text&node=40:22.0.1.1.3.3.1.10.18&idno=40
Note on B178: Enter NOx emission rate of the CHP system. Parts per Million (ppm) values are used for some turbine and boiler systems. The ppm value represents the concentration of NOx molecules in the exhaust.
Note on B179: Enter NOx emission rate of the CHP system. Grams of NOx per Horsepower-hour of production (gm/hp-hr) are most commonly used with engines.
Note on B180: Enter NOx emission rate for the CHP system. Pounds of NOx per MMBtu (lb/MMBtu) is most commonly used with boilers. The MMBtu represents the fuel input rate of the CHP system.
Note on B181: Enter NOx emission rate for the CHP system. Pounds of NOx per MegaWatt-Hour (lb/MWh) is occasionally used with various CHP technologies. The MWh represents the electrical output rating of the CHP system.
Note on B187: Enter NOx emission rate for the duct burners in lb per MMBtu on a fuel input basis. The average NOx emission rate for new duct burners is 0.10 lb/MMBtu. The NOx emission rate is for the duct burner(s) alone and does not include NOx from the CHP unit (usually a combustion turbine).
Note on B188: Enter NOx emission rate for the duct burners on a ppm @15% O2 basis The average NOx emission rate for new duct burners is 25 ppm. The NOx emission rate is for the duct burner(s) alone and does not include NOx from the CHP unit (usually a combustion turbine).
Note on B192: The CO2 emission rate for fuels is primarily based on the type of fuel. Typical values: Natural gas: 116.9 lb/MMBtu Oil: 163.1 lb/MMBtu Coal (Industrial - Mixed Use): 207.1 lb/MMBtu Propane: 139 lb/MMBtu The fuel-specific values come from EPA’s Mandatory Greenhouse Gas Reporting Rule. http://ecfr.gpoaccess.gov/cgi/t/text/textidx?c=ecfr&sid=69252b18e978de71ebe95c500dd9e47c&rgn=div9&view=text&node=40:22.0.1.1.3.3.1.10.18&idno=40
Note on B200: Enter value for sulfur content of boiler fuel The first option (1.0%) is in the normal range for commercial facilities using coal. The high-sulfur option (0.15%, 1500 ppm) is higher than average for most commercial applications and may not be appropriate for some areas. The low-sulfur option (0.05%, 500 ppm) is typical for an application where sulfur emissions are limited. Sulfur contents above 2.5% are unusual in units of this size. Information on fuels can be found at: http://eia.doe.gov/indexnjava.html
Note on B201: Enter value for sulfur content of boiler fuel The first option (1.0%) is in the normal range for commercial facilities using coal. The high-sulfur option (0.15%, 1500 ppm) is higher than average for most commercial applications and may not be appropriate for some areas. The low-sulfur option (0.05%, 500 ppm) is typical for an application where sulfur emissions are limited. This entry represents the sulfur content as Parts Per Million (ppm). Information on fuels can be found at: http://eia.doe.gov/indexnjava.html
Note on B206: Enter NOx emission ratefor the displaced boiler. Pounds of NOx per MMBtu (lb/MMBtu) is most commonly used with boilers. The MMBtu represents the fuel input rate of the CHP system.

## Results
CHP Results
The results generated by the CHP Energy and Emissions Savings Calculator are intended for educational and outreach purposes only;
it is not designed for use in developing emission inventories or preparing air permit applications.
The results of this analysis have not been reviewed or endorsed by the EPA CHP Partnership.
Table 1: Annual Energy Savings
| CHP System | Displaced Electricity Production | Displaced Thermal Production | Fuel Savings | Percent Savings
Fuel Consumption (MMBtu/year) | 0 | 0 | 0 | 0 | -
Equal to the annual energy consumption of this many passenger vehicles: |  |  |  | -
Equal to the annual energy consumption from the generation of electricity for this many homes: |  |  |  | -
Table 2: Annual Emissions Savings
| CHP System | Displaced Electricity Production | Displaced Thermal Production | Emissions Savings | Percent Savings
NOx (tons/year) | - | - | - | - | -
SO2 (tons/year) | - | - | - | - | -
CO2 (tons/year) | - | - | - | - | -
CH4 (tons/year) | - | - | - | - | -
N2O (tons/year) | - | - | - | - | -
Total GHGs (CO2e tons/year) | - | - | - | - | -
Carbon (metric tons/year) | - | - | - | - | -
Equal to the annual GHG emissions from this many passenger vehicles: |  |  |  | -
Equal to the annual GHG emissions from the generation of electricity for this many homes: |  |  |  | -
| Equal to the annual greenhouse |  |  | Equal to the annual greenhouse
| gas emissions from | gas emissions from the generation of
The results of this analysis have not been reviewed or endorsed by the EPA CHP Partnership.
Table 3: CHP Technology and Generation Profile
CHP Technology:
Fuel:
Unit Capacity: | 0 | kW
Number of Units: | 1
Total CHP Capacity: | 0 | kW
Operation: | 0 | hours per year
Heat Rate: | 0 | Btu/kWh HHV
CHP Fuel Consumption: | 0 | MMBtu/year
Duct Burner Fuel Consumption: | 0 | MMBtu/year
Total Fuel Consumption: | 0 | MMBtu/year
Total CHP Generation: | 0 | MWh/year
Useful CHP Thermal Output: | 0 | MMBtu/year for thermal applications (non-cooling)
| 0 | MMBtu/year for electric applications (cooling and electric heating)
| 0 | MMBtu/year Total
Table 4: Displaced Thermal Energy
Displaced On-Site Production for
Thermal (non-cooling) Applications: |  | There is no displaced thermal production
Displaced Electric Service (cooling and electric heating):
There is no displaced cooling service
Table 5: Displaced Electricity
Displaced Electricity Profile: | AVERT Uniform EE Factors (2022 Data)
eGRID/NERC Region: | AVERT - National Average
Distribution Losses: | 0% | [5 empty] | Update to 0 even if user selects eomthing else
Displaced Electricity Production: | 0 | MWh/year CHP generation
| 0 | MWh/year Displaced Electric Demand (cooling)
| 0 | MWh/year Displaced Electric Demand (electric heating)
| 0 | MWh/year Transmission Losses
| 0 | MWh/year Total
The results of this analysis have not been reviewed or endorsed by the EPA CHP Partnership.
Table 6: Annual Analysis for CHP
|  | Duct Burners (if applicable) | Total Emissions from CHP System
NOx (tons/year) | 0 | - | -
SO2 (tons/year) | 0 | - | -
CO2 (tons/year) | 0 | - | -
CH4 (tons/year) | - | 0 | -
N2O (tons/year) | - | 0 | -
Total GHGs (CO2e tons/year) | - | - | -
Carbon (metric tons/year) | 0 | - | -
Fuel Consumption (MMBtu/year) | 0 | 0 | 0
Table 7: Annual Analysis for Displaced Thermal Production (non-cooling)
Total Displaced Emissions from Thermal Production
NOx (tons/year) | 0
SO2 (tons/year) | 0
CO2 (tons/year) | 0
CH4 (tons/year) | 0
N2O (tons/year) | 0
Total GHGs (CO2e tons/year) | 0
Carbon (metric tons/year) | 0
Fuel Consumption (MMBtu/year) | 0
Table 8: Annual Analysis for Displaced Electricity Production
| Displaced CHP Electricity Generation | Displaced Electricity for Cooling | Displaced Electricity for Heating | Transmission Losses | Total Displaced Emissions from Electricity Generation
NOx (tons/year) | 0 | 0 | 0 | 0 | 0
SO2 (tons/year) | 0 | 0 | 0 | 0 | 0
CO2 (tons/year) | 0 | 0 | 0 | 0 | 0
CH4 (tons/year) | 0 | 0 | 0 | 0 | 0
N2O (tons/year) | 0 | 0 | 0 | 0 | 0
Total GHGs (CO2e tons/year) | 0 | 0 | 0 | 0 | 0
Carbon (metric tons/year) | 0 | 0 | 0 | 0 | 0
Fuel Consumption (MMBtu/year) | 0 | 0 | 0 | 0 | 0
Table 9: Emission Rates for Displaced Electricity
| CHP System including Duct Burners |  | Displaced Electricity Production
NOx (lb/MWh) | - | - | 0.7
SO2 (lb/MWh) | - | - | 0.67
CO2 (lb/MWh) | - | - | 1438
Table 10: Emission Rates for Displaced Thermal
Displaced Thermal Production
NOx (lb/MMBtu) | 0
SO2 (lb/MMBtu) | 0
CO2 (lb/MMBtu) | 0
The results of this analysis have not been reviewed or endorsed by the EPA CHP Partnership.
Figure 1. Conventional Production Energy Flow Schematic |  |  | Figure 2. CHP System Energy Flow Schematic
Total Emissions for Conventional Production |  |  |  | Total Emissions for CHP System
. tons of NOx |  |  |  | #VALUE!
. tons of SO2
tons of CO2e
MWh
MMBtu | Electricity to Facility |  | MMBtu
Fuel consumption |  |  | Fuel Consumption |  |  | MWh
Central Station | No Cooling |  |  | CHP |  | Electricity
Power Plant |  |  |  | System |  | to Facility
MWh
Transmission Losses
Power Plant Emissions |  |  | CHP Emissions |  | Thermal Energy from CHP
No
Thermal
Applications
On-Site Thermal | No
Production | Thermal Applications |  |  | Absorption
|  |  |  | Chiller |  | No Cooling
On-Site Thermal Emissions
Return to
Input Screen
Return to
Input Screen
Return to
Input Screen
Note on E13: Calculated from EPA GHG Equivalencies Calculator - Calculations and References: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references#vehicles
Note on E14: Calculated from EPA GHG Equivalencies Calculator - Calculations and References: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references#vehicles
Note on E30: Calculated from EPA GHG Equivalencies Calculator - Calculations and References: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references#vehicles
Note on E31: Calculated from EPA GHG Equivalencies Calculator - Calculations and References: https://www.epa.gov/energy/greenhouse-gases-equivalencies-calculator-calculations-and-references#vehicles

## SubThermalCalculator
Thermal Calculator
Value | Units | Description
Calculate the Power to Heat Ratio by completing the
entries in one of the following boxes:
0 | MMBtu/hr | Thermal output from a single unit
OR
0 | lb/hr | Steam consumed in process
1000 | Btu/lb | Enthalpy (a common value is 1,000 Btu/lb)
0 | MMBtu/hr | calculated
OR
0 | MMBtu/hr | Fuel consumed in thermal process (often a boiler)
0% |  | Efficiency of thermal converter
0 | MMBtu/hr | calculated
Results
0 | MMBtu/hr | thermal output
0 | kW | thermal output
Reset Thermal Calculator
Copy this Power to Heat Ratio to the Input Screen

## SubGenSources
Generation Sources
Existing Generation Sources |  |  |  |  | Heat Rate
Name | Code | NOx lb/MWh | SO2 lb/MWh | CO2 lb/MWh | Btu/kWh
AVERT Uniform EE | 1 | 0.7 | 0.67 | 1438 | 8934 | EPA AVERT 2022 (released April 2023), https://www.epa.gov/statelocalenergy/avoided-emission-factors-generated-avert-0
EGrid Annual Average | 2 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
EGrid Annual Fossil | 3 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
EGrid Annual Non-Baseload | 4 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
EGrid Annual Coal | 5 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
EGrid Annual Oil | 6 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
EGrid Annual Natural Gas | 7 | n/a | n/a | n/a | n/a | EPA eGRID2021 (released January 2023), http://www.epa.gov/energy/egrid
Coal Boiler 3.8 lb/MWh NOx | 8 | 3.8 | 5 | 1967.45 | 9500 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Coal Boiler 1.5 lb/MWh NOx | 9 | 1.5 | 2.5 | 1967.45 | 9500 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Coal Boiler with SCR 0.8 lb/MWh NOx | 10 | 0.8 | 1 | 1967.45 | 9500 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Gas Boiler 0.77 lb/MWh NOx | 11 | 0.77 | 0.0062369 | 1285.9 | 11000 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Gas Turbine Peaker 25 ppm | 12 | 1.1029 | 0.0068039 | 1402.8 | 12000 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Gas combined-cycle 9 ppm | 13 | 0.26471 | 0.0045359 | 935.2 | 8000 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Gas combined-cycle 3 ppm | 14 | 0.077206 | 0.0039689 | 818.3 | 7000 | AP 42, Fifth Edition, Compilation of Air Pollutant Emission Factors, Volume 1: Stationary Point and Area Sources. https://www.epa.gov/air-emissions-factors-and-quantification/ap-42-compilation-air-emission-factors
Please enter emission rates for the new generation sources:
User Defined Generation Sources |  |  |  |  | Heat Rate
Name | Code | NOx lb/MWh | SO2 lb/MWh | CO2 lb/MWh | Btu/kWh
User Source 1 | 15 | 0 | 0 | 0 | 0
User Source 2 | 16 | 0 | 0 | 0 | 0
User Source 3 | 17 | 0 | 0 | 0 | 0
Click here to use the rates that have been entered here to define a user source in Input 23,
and Return to Input Screen
Reset this
Generation Sources
Screen

## Biomass and Coal Data
Biomass and Coal Data
Note: The data in these tables are not used in any calculations within the tool, but are only provided as a reference for users entering biomass or coal data.
Biomass
Heat Content & Emission Rates for Biomass Fuels
| Heat Content (HHV) |  | CO2 Emission Rate* |  | NOx Emission Rate** |  | Sulfur Content**
Biomass Fuel Source
Wood and Wood Residuals | 8740 | Btu/lb | 206.7 | lb/MMBtu | 0.49 | lb/MMBtu | 0.025 | lb/MMBtu
Agricultural Byproducts | 4125 | Btu/lb | 260.4 | lb/MMBtu
Solid Byproducts | 5195 | Btu/lb | 232.5 | lb/MMBtu
Biogas | 655 | Btu/scf | 114.7 | lb/MMBtu
Landfill Gas | 485 | Btu/scf | 114.7 | lb/MMBtu
Biodiesel | 128000 | Btu/gal | 162.7 | lb/MMBtu
Ethanol | 84000 | Btu/gal | 150.8 | lb/MMBtu
*CO2 Emissions data from EPA Mandatory GHG Reporting Rule, 40 CFR 98, Subpart C, Table C-1
**NOX and Sulfur emissions data for dry wood fuels from AP-42. Rates for Agricultural Byproducts and Solid Byproducts depend on the composition of the fuels, and for NOx, the combustion temperature. Gaseous and liquid biomass fuels contain trace amounts of Sulfur, and their NOx content is variable, depending on prime mover, combustion temperature, and post-combustion emission controls.
Coal
| Heat Content (HHV) |  | CO2 Emission Rate
Coal Type
Anthracite | 12545 | Btu/lb | 228.6 | lb/MMBtu
Bituminous | 12465 | Btu/lb | 205.6 | lb/MMBtu
Sub-bituminous | 8625 | Btu/lb | 214.2 | lb/MMBtu
Lignite | 7105 | Btu/lb | 215.4 | lb/MMBtu
Industrial Mixed Use | 11175 | Btu/lb | 208.7 | lb/MMBtu
Commercial Mixed Use | 10695 | Btu/lb | 207.8 | lb/MMBtu
*Emissions Data from EPA Mandatory GHG Reporting Rule, Part 98, Subpart C, Table C-1
For an expanded list of emissions factors and heat content values, please see Table C-1 in 40 CFR 98:
http://www.ecfr.gov/cgi-bin/text-idx?tpl=/ecfrbrowse/Title40/40cfr98_main_02.tpl
Return to Input Screen

## Maps
AVERT Regions Map
eGRID Subregions Map
NERC Interconnections Map
Return to
Input Screen
Return to
Input Screen
Return to
Input Screen

## Lists (hidden)
CHP Pick list lookups
A1 | CHP technology
1 | Recip Engine - Rich Burn | Recip Engine - Rich Burn
2 | Recip Engine - Lean Burn | Recip Engine - Lean Burn
3 | Recip Engine - Diesel | Recip Engine - Diesel
4 | Microturbine | Microturbine
5 | Combustion Turbine | Combustion Turbine
6 | Boiler / Steam Turbine | Boiler / Steam Turbine
7 | Fuel Cell | Fuel Cell
8 | Other Prime Mover | Other
9 | Waste Heat to Power (Power Only) | Waste Heat to Power
10 | Waste Heat to Power (Power and Thermal) | Waste Heat to Power
B3 | Operating profile of CHP | Hours
1 | 5 days per week, 8 hours per day - 2,080 hours | 2080
2 | 5 days per week, 16 hours per day - 4,160 hours | 4160
3 | 7 days per week - 16 hours per day - 5,840 hours | 5840
4 | 7 days per week, 24 hours per day, 8,760 hours | 8760
5 | I will enter a value
B5 | Profile of Displaced Electricity
1 | AVERT Uniform EE Factors (2022 Data) | A | 1 | AVERT
2 | eGRID All Sources (2021 Data) | E | 1 | Egrid State Average
3 | eGRID Fossil Fuel (2021 Data) | E | 2 | Egrid State Average
4 | eGRID Non-Baseload (2021 Data) | E | 3 | Egrid State Average
5 | eGRID Coal (2021 Data) | E | 4 | Egrid State Average
6 | eGRID Oil (2021 Data) | E | 5 | Egrid State Average
7 | eGRID Gas (2021 Data) | E | 6 | Egrid State Average
8 | Coal Boiler 3.8 lb/MWh NOx | D | 1 | Defined
9 | Coal Boiler 1.5 lb/MWh NOx | D | 2 | Defined
10 | Coal Boiler with SCR 0.8 lb/MWh NOx | D | 3 | Defined
11 | Gas Boiler 0.77 lb/MWh NOx | D | 4 | Defined
12 | Gas Turbine Peaker 25 ppm | D | 5 | Defined
13 | Gas combined-cycle 9 ppm | D | 6 | Defined
14 | Gas combined-cycle 3 ppm | D | 7 | Defined
15 | User Source 1 | U | 1 | User Profile
16 | User Source 2 | U | 2 | User Profile
17 | User Source 3 | U | 3 | User Profile
B8 | Egrid profile
1 | eGRID State Averages All Sources (2021 Data)
2 | eGRID State Average Fossil (2021 Data)
3 | eGRID State Averages Coal (2021 Data)
4 | eGRID State Averages Oil (2021 Data)
5 | eGRID State Averages Gas (2021 Data)
D2 | Displaced Thermal Source | CO2 rate |  |  | Heat Content
1 | Existing Gas Boiler | 116.9 |  |  | 1028 | Btu/cf
2 | Existing Distillate Oil Boiler | 163.1 |  |  | 138000 | Btu/gal
3 | Existing Residual Oil Boiler | 163.1 |  |  | 150000 | Btu/gal
4 | Existing Coal Boiler | 207.1 |  |  | 11175 | Btu/lb
5 | New Gas Boiler | 116.9 |  |  | 1028 | Btu/cf
6 | New Distillate Oil Boiler | 163.1 |  |  | 138000 | Btu/gal
7 | New Residual Oil Boiler | 163.1 |  |  | 150000 | Btu/gal
8 | New Coal Boiler | 207.1 |  |  | 11175 | Btu/lb
9 | Electric Resistence or Heat Pump | 0 |  |  | 0
10 | Existing Propane Boiler | 139 |  |  | 91600 | Btu/gal
11 | New Propane Boiler | 139 |  |  | 91600 | Btu/gal
12 | Other | 0 |  |  | 138000 | Btu/gal
B6 | State | Region | Grid Loss %
1 | AVERT - National Average |  |  |  | 0 | 0
2 | AVERT - California
3 | AVERT - Carolinas
4 | AVERT - Central
5 | AVERT - Florida
6 | AVERT - Mid-Atlantic
7 | AVERT - Midwest
8 | AVERT - New England
9 | AVERT - New York
10 | AVERT - Northwest
11 | AVERT - Rocky Mountains
12 | AVERT - Southeast
13 | AVERT - Southwest
14 | AVERT - Tennessee
15 | AVERT - Texas
16 | eGRID - US Average | 1 | 0.045
17 | AKGD - ASCC Alaska Grid | 5 | 0.044
18 | AKMS - ASCC Miscellaneous | 5 | 0.044
19 | AZNM - WECC Southwest | 3 | 0.044
20 | CAMX - WECC California | 3 | 0.044
21 | ERCT - ERCOT All | 4 | 0.044
22 | FRCC - FRCC All | 2 | 0.045
23 | HIMS - HICC Miscellaneous | 6 | 0.048
24 | HIOA - HICC Oahu | 6 | 0.048
25 | MROE - MRO East | 2 | 0.045
26 | MROW - MRO West | 2 | 0.045
27 | NEWE - NPCC New England | 2 | 0.045
28 | NWPP - WECC Northwest | 2 | 0.045
29 | NYCW - NPCC NYC/Westchester | 2 | 0.045
30 | NYLI - NPCC Long Island | 2 | 0.045
31 | NYUP - NPCC Upstate NY | 2 | 0.045
32 | RFCE - RFC East | 2 | 0.045
33 | RFCM - RFC Michigan | 2 | 0.045
34 | RFCW - RFC West | 3 | 0.044
35 | RMPA - WECC Rockies | 3 | 0.044
36 | SPNO - SPP North | 2 | 0.045
37 | SPSO - SPP South | 2 | 0.045
38 | SRMV - SERC Mississippi Valley | 2 | 0.045
39 | SRMW - SERC Midwest | 2 | 0.045
40 | SRSO - SERC South | 2 | 0.045
41 | SRTV - SERC Tennessee Valley | 2 | 0.045
42 | SRVC - SERC Virginia/Carolina | 2 | 0.045
43 | PRMS - Puerto Rico Miscellaneous | 1 | 0.045
44 | ASCC - Alaska Systems Coordinating Council | 5 | 0.044
45 | HICC - Hawaiian Islands Coordinating Council | 6 | 0.048
46 | MRO - Midwest Reliability Organization | 2 | 0.045
47 | NPCC - Northeast Power Coordinating Council | 2 | 0.045
48 | RFC - Reliability First Corporation | 2 | 0.045
49 | SERC - Southeastern Electric Reliability Corporation | 2 | 0.045
50 | TRE - Texas Regional Entity | 4 | 0.044
51 | WECC - Western Electricity Coordinating Council | 3 | 0.044
52 | PR - Puerto Rico | 1 | 0.045
A6 | Fuel used in CHP system | CO2 rate |  |  | Heat Content
1 | Natural Gas | 116.9 |  |  | 1028 | Btu/cf
2 | Diesel Fuel | 163.1 |  |  | 138000 | Btu/gal
3 | Distillate Oil | 163.1 |  |  | 138000 | Btu/gal
4 | Coal | 207.1 |  |  | 11175 | Btu/lb
5 | Propane | 139 |  |  | 91600 | Btu/gal
6 | Woody Biomass | 206.7 |  |  | 7500 | Btu/lb
7 | Other Fuel (including renewables) | 0 |  |  | 138000 | Btu/gal
8 | Waste Heat | 0
A7 | Fuel used in STM system | CO2 rate |  |  | Heat Content
1 | Natural Gas | 116.9 |  |  | 1028 | Btu/cf
2 | Diesel Fuel | 163.1 |  |  | 138000 | Btu/gal
3 | Distillate Oil | 163.1 |  |  | 138000 | Btu/gal
4 | Coal | 207.1 |  |  | 11175 | Btu/lb
5 | Propane | 139 |  |  | 91600 | Btu/gal
6 | Woody Biomass | 206.7 |  |  | 7500 | Btu/lb
7 | Other Fuel | 0 |  |  | 138000 | Btu/gal
A8 | Does the System provide cooling
1 | Yes
2 | No
A9 | CHP: What Cooling Technology Does this System Use?
1 | #N/A |  | #N/A | Single-Effect Absorption Chiller
2 | #N/A |  | #N/A | Double-Effect Absorption Chiller
3 | I Will Enter a Value |  |  | I Will Enter a Value
C4 | Does the System have duct burners
1 | Yes
2 | No
H1 | Does the System Provide Heating Cooling or Both?
1 | Heating Only
2 | Cooling Only
3 | Heating and Cooling
H2 | If Heating and Cooling: Does the System Provide Simultaneous Heating and Cooling?
1 | Yes
2 | No
H3 | What is the Efficiency of the Cooling System that is Being Displaced?
1 | 1.30 kW/ton (COP=2.7) 1990 Vintage, Air-cooled with condenser, <150 tons
2 | 1.41 kW/ton (COP=2.5) 1990 Vintage, Air-cooled with condenser, >150 tons
3 | 0.93 kW/ton (COP=3.8) 1990 Vintage, Water-cooled, <150 tons
4 | 0.84 kW/ton (COP=4.2) 1990 Vintage, Water-cooled, 150-300 tons
5 | 0.75 kW/ton (COP=4.7) 1990 Vintage, Water-cooled, >300 tons
6 | 1.25 kW/ton (COP=2.8) 2010 ASHRAE Standard, Air-cooled with condenser
7 | 0.78 kW/ton (COP=4.54) 2010 ASHRAE Standard, Water-cooled, positive displacement <150 tons
8 | 0.68 kW/ton (COP=5.17) 2010 ASHRAE Standard, Water-cooled, positive displacement 150-300 tons
9 | 0.62 kW/ton (COP=5.67) 2010 ASHRAE Standard, Water-cooled, positive displacement >300 tons
10 | 0.63 kW/ton (COP=5.55) 2010 ASHRAE Standard, Water-cooled, centrifugal <300 tons
11 | 0.58 kW/ton (COP=6.11) 2010 ASHRAE Standard, Water-cooled, centrifugral >300 tons
12 | 1.19 kW/ton (COP=2.96) 2015 ASHRAE Standard, Air-cooled with condenser
13 | 1.72 kW/ton (COP=4.88) 2015 ASHRAE Standard, Water-cooled, positive displacement <150 tons
14 | 0.66 kW/ton (COP=5.33) 2015 ASHRAE Standard, Water-cooled, positive displacement 150-300 tons
15 | 0.61 kW/ton (COP=5.77) 2015 ASHRAE Standard, Water-cooled, positive displacement >300 tons
16 | 0.70 kW/ton (COP=5.06) 2015 ASHRAE Standard, Water-cooled, centrifugal <150 tons
17 | 0.64 kW/ton (COP=5.54) 2015 ASHRAE Standard, Water-cooled, centrifugal 150-300 tons
18 | 0.60 kW/ton (COP=5.91) 2015 ASHRAE Standard, Water-cooled, centrifugral >300 tons
19 | I will enter a value
B7 | US Interconnect Power Grid Region | T&D Loss %
1 | US Average | 4.5%
2 | Eastern Interconnect | 4.5%
3 | Western Interconnect | 4.4%
4 | ERCOT | 4.4%
5 | Alaska | 4.4%
6 | Hawaii | 4.8%
7 | I will enter a value

## STMTech (hidden)
Displaced Thermal Calculation
Selected Thermal Source
0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A
| Fuel used in displaced boiler | Boiler Eff | NOx lb/MMBtu | Sulfur content | SO2 lb/MMBtu | CO2 lb/MMBtu |  | Fuel MMBtu/ton | CH4 lb/MMBtu | N2O lb/MMBtu
1 | Existing - Natural Gas | 80% | 0.1 | 7.097e-05% | 0.00058514 | 116.9 |  | 4.8513 | 0.002204 | 0.0002204
2 | Existing - Distillate Oil | 80% | 0.15 | 0.0487% | 0.051086 | 163.1 |  | 38.1316 | 0.006612 | 0.0013224
3 | Existing - Residual Oil | 83% | 0.2 | 0.1461% | 0.15352 | 163.1 |  | 38.0665 | 0.006612 | 0.0013224
4 | Existing - Coal | 85% | 0.4 | 1% | 1.9034 | 207.1 |  | 21.015 | 0.024244 | 0.0035264
5 | New - Natural Gas | 80% | 0.05 | 7.097e-05% | 0.00058514 | 116.9 |  | 4.8513 | 0.002204 | 0.0002204
6 | New - Distillate Oil | 80% | 0.05 | 0.0487% | 0.051086 | 163.1 |  | 38.1316 | 0.006612 | 0.0013224
7 | New - Residual Oil | 83% | 0.1 | 0.0974% | 0.10235 | 163.1 |  | 38.0665 | 0.006612 | 0.0013224
8 | New - Coal | 85% | 0.1 | 1% | 1.9034 | 207.1 |  | 21.015 | 0.024244 | 0.0035264
9 | Electric Resistence or Heat Pump | 120% | 0 | 0% | 0 | 0 |  | 0 | 0 | 0
10 | Existing - Propane | 80% | 0.1 | 7.097e-05% | 0.000584 | 139 |  | 43.619 | 0.002204 | 0.0002204
11 | New - Propane | 80% | 0.1 | 7.097e-05% | 0.000584 | 139 |  | 43.619 | 0.002204 | 0.0002204
12 | Other | 80% | 0 | 0% | 0 | 160 |  | 38.0665 | 0.006612 | 0.0013224
Boiler Efficiency
0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Boiler Eff | NOx lb/MMBtu | Sulfur Content | SO2 lb/MMBtu | CO2 lb/MMBtu | CH4 lb/MMBtu | N2O lb/MMBtu
1 | Natural Gas | 80% | 0.1 | 0.0001% | 0.000584 | 116.9 | 0.002204 | 0.0002204
2 | Diesel Fuel | 80% | 0.15 | 0.0487% | 0.05 | 163.1 | 0.006612 | 0.0013224
3 | Distillate Oil | 80% | 0.15 | 0.0487% | 0.05 | 163.1 | 0.006612 | 0.0013224
4 | Coal | 85% | 0.1 | 1% | 1.9 | 207.1 | 0.024244 | 0.0035264
5 | Propane | 80% | 0.1 | 0.0001% | 0.000584 | 116.9 | 0.002204 | 0.0002204
6 | Woody Biomass | 83% | 0.165 | 0.001% | 0.00825 | 206.7 | 0.07 | 0.009
7 | Other | 80% | 0.1 | 0.0001% | 0 | 0 | 0 | 0

## CHPTech (hidden)
CHP Technologies
Selected
Technology
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| #N/A | Recip Rich Burn | Recip Lean Burn | Recip Diesel | Microturbine | Combustion Turbine | Boiler / Steam Turbine | Fuel Cell | Other | Waste Heat to Power
Capacity (kW) | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CapLow (kW) | #N/A | 5 | 500 | 90 | 30 | 1000 | 100 | 5 | 0 | 50
CapHigh (kW) | #N/A | 1200 | 5000 | 1600 | 1000 | 40000 | 15000 | 3000 | 0 | 10000
Misc | #N/A | Catalyst | 0 | 0 | #N/A | 0 | 0 | ClearEdge SOFC | 0
Fuel | #N/A | Natural Gas | Natural Gas | Diesel | Natural gas | Natural gas | Natural Gas | Natural Gas | #N/A | Waste Heat
% | #N/A | 23% | 34.96% | 29.28% | 22.54% | 21.4% | 0% | 30.01% | 0% | 0%
Btu/kWh HHV | #N/A | 14835 | 9760 | 11653.3333 | 15140 | 15945 | 0 | 11370 | 0
Btu/kWh LHV | #N/A | 13425.3394 | 8832.5792 | 10614.4703 | 13701.3575 | 14429.8643 | 0 | 10289.5928 | 0
P/H ratio | #N/A | 0.4 | 0.79 | 0.66 | 0.51 | 0.44 | 0 | 0.85 | 0
NOx ppm | #N/A | 0 | 0 | 0 | 12 | 42 | 0 | 3 | 0 | 0
NOx gm/hp-hr | #N/A | 0.15 | 0.7 | 3 | 0 | 0 | 0 | 0 | 0 | 0
NOx lb/MMBtu | #N/A | 0.031446 | 0.22305 | 0.80063 | 0.042272 | 0.15441 | #N/A | 0.0026385 | 0 | 0
NOx lb/MWh | #N/A | 0.4665 | 2.177 | 9.33 | 0.64 | 2.4621 | 0 | 0.03 | 0 | 0
SO2 lb/MMBtu | #N/A | 0.0006 | 0.0006 | 0 | 0 | 0.0006 | #N/A | 0.0001 | 0 | 0
SO2 lb/MWh | #N/A | 0.008901 | 0.005856 | 0 | 0 | 0.009567 | 0 | 0.001137 | 0 | 0
CO2 lb/MWh | #N/A | 1734.2115 | 1140.944 | 0 | 0 | 0 | 0 | 1360 | 0 | 0
Detailed
Recip Rich Burn
| 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Recip Rich Burn | Recip Rich Burn | Recip Rich Burn | Recip Rich Burn | Recip Rich Burn | Recip Rich Burn | Recip Rich Burn | Recip Rich Burn
Capacity (kW) | 0 | 5 | 50 | 100 | 150 | 300 | 800 | 1200
CapLow (kW) | 5
CapHigh (kW) | 1200
Misc | Catalyst | Catalyst | Catalyst | Catalyst | Catalyst | Catalyst | Catalyst | Catalyst
Fuel | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas
% | 23% | 23% | 27.88% | 28.43% | 30.41% | 31.77% | 32.5% | 33.57%
Btu/kWh HHV | 14835 | 14835 | 12240 | 12000 | 11220 | 10741 | 10500 | 10164
Btu/kWh LHV | 13425.3394 | 13425.3394 | 11076.9231 | 10859.7285 | 10153.8462 | 9774.31 | 9555 | 9249.24
P/H ratio | 0.4 | 0.4 | 0.63 | 0.52 | 0.69 | 0.71 | 0.72 | 0.75
NOx ppm | 0
NOx gm/hp-hr | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
NOx lb/MMBtu | 0.031446 | 0.031446 | 0.038113 | 0.038875 | 0.041578 | 0.043432 | 0.044429 | 0.045897
NOx lb/MWh | 0.4665 | 0.4665 | 0.4665 | 0.4665 | 0.4665 | 0.4665 | 0.4665 | 0.4665
SO2 lb/MMBtu | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.00056699
SO2 lb/MWh | 0.008901 | 0.008901 | 0.007344 | 0.0072 | 0.006732 | 0.0064446 | 0.0063 | 0.0057629
CO2 lb/MWh | 1734.2115 | 1734.2115 | 1430.856 | 1402.8 | 1311.618 | 1255.6229 | 1227.45 | 1188.1716
Detailed
Recip Lean Burn
| 0 | 2 | 2 | 2
| Recip Lean Burn | Recip Lean Burn | Recip Lean Burn | Recip Lean Burn
Capacity (kW) | 0 | 500 | 3000 | 5000
CapLow (kW) | 500
CapHigh (kW) | 5000
Misc | 0
Fuel | Natural Gas | Natural Gas | Natural Gas | Natural Gas
% | 34.96% | 34.96% | 35.95% | 38.96%
Btu/kWh HHV | 9760 | 9760 | 9492 | 8758
Btu/kWh LHV | 8832.5792 | 8832.5792 | 8590.0452 | 7925.7919
P/H ratio | 0.79 | 0.79 | 0.97 | 1.12
NOx ppm | 0
NOx gm/hp-hr | 0.7 | 0.7 | 0.7 | 0.5
NOx lb/MMBtu | 0.22305 | 0.22305 | 0.22935 | 0.17755
NOx lb/MWh | 2.177 | 2.177 | 2.177 | 1.555
SO2 lb/MMBtu | 0.0006 | 0.0006 | 0.0006 | 0.0006
SO2 lb/MWh | 0.005856 | 0.005856 | 0.0056952 | 0.0052548
CO2 lb/MWh | 1140.944 | 1140.944 | 1109.6148 | 1023.8102
Detailed
Recip Diesel
| 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Recip Diesel | Recip Diesel | Recip Diesel | Recip Diesel | Recip Diesel | Recip Diesel | Recip Diesel | Recip Diesel
Capacity (kW) | 0 | 90 | 160 | 320 | 545 | 680 | 1100 | 1600
CapLow (kW) | 90
CapHigh (kW) | 1600
Misc | 0
Fuel | Diesel | Diesel | Diesel | Diesel | Diesel | Diesel | Diesel | Diesel
% | 29.28% | 29.28% | 31.4% | 34.7% | 33.11% | 34.31% | 35.37% | 35.42%
Btu/kWh HHV | 11653.3333 | 11653.3333 | 10867.5 | 9832.5 | 10305.6881 | 9944.1176 | 9647.4545 | 9634.125
Btu/kWh LHV | 10614.4703 | 10614.4703 | 9898.6919 | 8955.9593 | 9386.9639 | 9057.6265 | 8787.4101 | 8775.2689
P/H ratio | 0.66 | 0.66 | 0.7 | 0.7 | 0.72 | 0.72 | 0.84 | 0.84
NOx ppm | 0
NOx gm/hp-hr | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
NOx lb/MMBtu | 0.80063 | 0.80063 | 0.85852 | 0.94889 | 0.90533 | 0.93824 | 0.96709 | 0.96843
NOx lb/MWh | 9.33 | 9.33 | 9.33 | 9.33 | 9.33 | 9.33 | 9.33 | 9.33
SO2 lb/MMBtu | 0
SO2 lb/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO2 lb/MWh | 0
Detailed
Microturbine
| 0 | 4 | 4 | 4 | 4
| Microturbine | Microturbine | Microturbine | Microturbine | Microturbine
Capacity (kW) | 0 | 30 | 65 | 200 | 1000
CapLow (kW) | 30
CapHigh (kW) | 1000
Misc | #N/A
Fuel | Natural gas | Natural gas | Natural gas | Natural gas | Natural gas
% | 22.54% | 22.54% | 26.17% | 29.98% | 29.98%
Btu/kWh HHV | 15140 | 15140 | 13039 | 11380 | 11380
Btu/kWh LHV | 13701.3575 | 13701.3575 | 11800 | 10298.6425 | 10298.6425
P/H ratio | 0.51 | 0.51 | 0.54 | 0.71 | 0.71
NOx ppm | 12 | 12 | 9 | 9 | 9
NOx gm/hp-hr | 0
NOx lb/MMBtu | 0.042272 | 0.042272 | 0.035279 | 0.035149 | 0.035149
NOx lb/MWh | 0.64 | 0.64 | 0.46 | 0.4 | 0.4
SO2 lb/MMBtu | 0
SO2 lb/MWh | 0 | 0 | 0 | 0 | 0
CO2 lb/MWh | 0
Detailed
Combustion Turbine
| 0 | 5 | 5 | 5 | 5 | 5
| Combustion Turbine | Combustion Turbine | Combustion Turbine | Combustion Turbine | Combustion Turbine | Combustion Turbine
Capacity (kW) | 0 | 1000 | 5000 | 10000 | 25000 | 40000
CapLow (kW) | 1000
CapHigh (kW) | 40000
Misc | 0
Fuel | Natural gas | Natural gas | Natural gas | Natural gas | Natural gas | Natural gas
% | 21.4% | 21.4% | 28.9% | 29.1% | 34.31% | 37.01%
Btu/kWh HHV | 15945 | 15945 | 11806 | 11725 | 9945 | 9220
Btu/kWh LHV | 14429.8643 | 14429.8643 | 10684.1629 | 10610.8597 | 9000 | 8343.8914
P/H ratio | 0.44 | 0.44 | 0.62 | 0.69 | 0.94 | 1.07
NOx ppm | 42 | 42 | 25 | 25 | 15 | 15
NOx gm/hp-hr | 0
NOx lb/MMBtu | 0.15441 | 0.15441 | 0.091912 | 0.091912 | 0.055147 | 0.055147
NOx lb/MWh | 2.4621 | 2.4621 | 1.0851 | 1.0777 | 0.54844 | 0.50846
SO2 lb/MMBtu | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0006
SO2 lb/MWh | 0.009567 | 0.009567 | 0.0070836 | 0.007035 | 0.005967 | 0.005532
CO2 lb/MWh | 0
Detailed
Boiler / Steam Turbine
| 0 | 6 | 6 | 6 | 6
| Boiler / Steam Turbine | Boiler / Steam Turbine | Boiler / Steam Turbine | Boiler / Steam Turbine | Boiler / Steam Turbine
Capacity (kW) | 0 | 100 | 500 | 3000 | 15000
CapLow (kW) | 100
CapHigh (kW) | 15000
Misc | 0
Fuel | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas
% | 0%
Btu/kWh HHV | 0
Btu/kWh LHV | 0
P/H ratio | 0
NOx ppm | 0
NOx gm/hp-hr | 0
NOx lb/MMBtu | #N/A
NOx lb/MWh | 0
SO2 lb/MMBtu | #N/A | 0.0006 | 0.0006 | 0.0006 | 0.0006
SO2 lb/MWh | 0 | 0 | 0 | 0 | 0
CO2 lb/MWh | 0 | 0 | 0 | 0 | 0
Detailed
Fuel Cell
| 0 | 7 | 7 | 7 | 7 | 7
| Fuel Cell | Fuel Cell | Fuel Cell | Fuel Cell | Fuel Cell | Fuel Cell
Capacity (kW) | 0 | 5 | 300 | 400 | 1500 | 3000
CapLow (kW) | 5
CapHigh (kW) | 3000
Misc | ClearEdge SOFC | ClearEdge SOFC | FuelCell MCFC | UTC PAFC | FuelCell MCFC | FuelCell MCFC
Fuel | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas
% | 30.01% | 30.01% | 42.53% | 38% | 42.53% | 42.53%
Btu/kWh HHV | 11370 | 11370 | 8022 | 8980 | 8022 | 8022
Btu/kWh LHV | 10289.5928 | 10289.5928 | 7259.7285 | 8126.6968 | 7259.7285 | 7259.7285
P/H ratio | 0.85 | 0.85 | 1.27 | 1.42 | 1.27 | 1.27
NOx ppm | 3 | 3
NOx gm/hp-hr | 0
NOx lb/MMBtu | 0.0026385 | 0.0026385 | 0.0012466 | 0.0022272 | 0.0012466 | 0.0012466
NOx lb/MWh | 0.03 | 0.03 | 0.01 | 0.02 | 0.01 | 0.01
SO2 lb/MMBtu | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001
SO2 lb/MWh | 0.001137 | 0.001137 | 0.0008022 | 0.000898 | 0.0008022 | 0.0008022
CO2 lb/MWh | 1360 | 1360 | 1170 | 1135 | 950 | 890
User Defined
CHP
| 0 | 8
| Other | Other
Capacity (kW) | 0 | 0
CapLow (kW) | 0
CapHigh (kW) | 0
Misc | 0
Fuel | #N/A | #N/A
% | 0% | 0%
Btu/kWh HHV | 0 | 0
Btu/kWh LHV | 0 | 0
P/H ratio | 0 | 0
NOx ppm | 0 | 0
NOx gm/hp-hr | 0 | 0
NOx lb/MMBtu | 0 | 0
NOx lb/MWh | 0 | 0
SO2 lb/MMBtu | 0
SO2 lb/MWh | 0 | 0
CO2 lb/MWh | 0
Duct Burner
| 0 | 1 | 2 | 3 | 4 | 5 | 6 |  | Duct Burner emissions data from:
NOx lb/MMBtu | #N/A | 0.08 | 0.08 | 0.08 | 0.08 |  |  |  | Solar Turbines Inc
NOx ppm | #N/A | 21.76 | 20.64 | 20.64 | 21.76
| Absorbtion Cooler | Recip Engine - Rich Burn, natural gas | Recip Engine - Lean Burn, natural gas | Recip Engine - Diesel | Microturbine | Combustion Turbine | Boiler / Steam Turbine | Fuel Cell | Other |  | Absorption Chiller Data from:
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  | Application Engineering Manual for Integrated Systems Design
Single Effect | #N/A | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 |  | American Gas Cooling Center
Double Effect | #N/A | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 |  | March 1999
Note on C110: B Hedman: Capstone C30 with on board compressor
Note on D110: B Hedman: Capstone C65
Note on E110: B Hedman: Capstone C200
Note on F110: B Hedman: Capstone C1000
Note on D112: ICF: Hot water thermal
Note on E112: ICF: Hot water thermal
Note on F112: ICF: Hot water thermal
Note on C134: ICF: Solar Saturn
Note on D134: ICF: Solar Taurus
Note on E134: ICF: Solar Titan
Note on F134: ICF: GE LM2500
Note on G134: ICF: GE LM1600
Note on D184: ICF: Hot water version 120 F
Note on E184: ICF: Hot water - 120 F
Note on F184: ICF: Hot water 120 F
Note on G184: ICF: Hot water 120 F
Note on C189: ICF: Fuel Cells remove sulfur from fuel to prevent contamination
Note on D189: ICF: Fuel Cells remove sulfur from fuel to prevent contamination
Note on E189: ICF: Fuel Cells remove sulfur from fuel to prevent contamination
Note on F189: ICF: Fuel Cells remove sulfur from fuel to prevent contamination
Note on G189: ICF: Fuel Cells remove sulfur from fuel to prevent contamination

## EGRID (hidden)
eGRID2021 Version 1.0 NERC Region File (Year 2023 Data) |  |  |  | SRNAMEPCAP | SRHTIAN | SRHTIOZ | SRHTIANT | SRHTIOZT | SRNGENAN | SRNGENOZ | SRNOXAN | SRNOXOZ | SRSO2AN | SRCO2AN | SRCH4AN | SRN2OAN | SRCO2EQA | SRHGAN | SRNOXRTA | SRNOXRTO | SRSO2RTA | SRCO2RTA | SRCH4RTA | SRN2ORTA | SRC2ERTA | SRHGRTA | SRNOXRA | SRNOXRO | SRSO2RA | SRCO2RA | SRCH4RA | SRN2ORA | SRC2ERA | SRHGRA | SRNOXCRT | SRNOXCRO | SRSO2CRT | SRCO2CRT | SRCH4CRT | SRN2OCRT | SRC2ECRT | SRHGCRT | SRCNOXRT | SRONOXRT | SRGNOXRT | SRFSNXRT | SRCNXORT | SRONXORT | SRGNXORT | SRFSNORT | SRCSO2RT | SROSO2RT | SRGSO2RT | SRFSS2RT | SRCCO2RT | SROCO2RT | SRGCO2RT | SRFSC2RT | SRCCH4RT | SROCH4RT | SRGCH4RT | SRFCH4RT | SRCN2ORT | SRON2ORT | SRGN2ORT | SRFN2ORT | SRCC2ERT | SROC2ERT | SRGC2ERT | SRFSC2ERT | SRCHGRT | SRFSHGRT | SRCNOXR | SRONOXR | SRGNOXR | SRFSNXR | SRCNXOR | SRONXOR | SRGNXOR | SRFSNOR | SRCSO2R | SROSO2R | SRGSO2R | SRFSS2R | SRCCO2R | SROCO2R | SRGCO2R | SRFSC2R | SRCCH4R | SROCH4R | SRGCH4R | SRFCH4R | SRCN2OR | SRON2OR | SRGN2OR | SRFN2OR | SRCC2ER | SROC2ER | SRGC2ER | SRFSC2ER | SRCHGR | SRFSHGR | SRNBNOX | SRNBNXO | SRNBSO2 | SRNBCO2 | SRNBCH4 | SRNBN2O | SRNBC2E | SRNBHG | SRGENACL | SRGENAOL | SRGENAGS | SRGENANC | SRGENAHY | SRGENABM | SRGENAWI | SRGENASO | SRGENAGT | SRGENAOF | SRGENAOP | SRGENATN | SRGENATR | SRGENATH | SRGENACY | SRGENACN | SRCLPR | SROLPR | SRGSPR | SRNCPR | SRHYPR | SRBMPR | SRWIPR | SRSOPR | SRGTPR | SROFPR | SROPPR | SRTNPR | SRTRPR | SRTHPR | SRCYPR | SRCNPR | SRNBGNCL | SRNBGNOL | SRNBGNGS | SRNBGNNC | SRNBGNHY | SRNBGNBM | SRNBGNWI | SRNBGNSO | SRNBGNGT | SRNBGNOF | SRNBGNOP | SRNBCLPR | SRNBOLPR | SRNBGSPR | SRNBNCPR | SRNBHYPR | SRNBBMPR | SRNBWIPR | SRNBSOPR | SRNBGTPR | SRNBOFPR | SRNBOPPR
|  |  |  | eGRID subregion nameplate capacity (MW) | eGRID subregion annual heat input from combustion (MMBtu) | eGRID subregion ozone season heat input from combustion (MMBtu) | eGRID subregion total annual heat input (MMBtu) | eGRID subregion total ozone season heat input (MMBtu) | eGRID subregion annual net generation (MWh) | eGRID subregion ozone season net generation (MWh) | eGRID subregion annual NOx emissions (tons) | eGRID subregion ozone season NOx emissions (tons) | eGRID subregion annual SO2 emissions (tons) | eGRID subregion annual CO2 emissions (tons) | eGRID subregion annual CH4 emissions (lbs) | eGRID subregion annual N2O emissions (lbs) | eGRID subregion annual CO2 equivalent emissions (tons) | eGRID subregion annual Hg emissions (lbs) | eGRID subregion annual NOx total output emission rate (lb/MWh) | eGRID subregion ozone season NOx total output emission rate (lb/MWh) | eGRID subregion annual SO2 total output emission rate (lb/MWh) | eGRID subregion annual CO2 total output emission rate (lb/MWh) | eGRID subregion annual CH4 total output emission rate (lb/MWh) | eGRID subregion annual N2O total output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent total output emission rate (lb/MWh) | eGRID subregion annual Hg total output emission rate (lb/MWh) | eGRID subregion annual NOx input emission rate (lb/MMBtu) | eGRID subregion ozone season NOx input emission rate (lb/MMBtu) | eGRID subregion annual SO2 input emission rate (lb/MMBtu) | eGRID subregion annual CO2 input emission rate (lb/MMBtu) | eGRID subregion annual CH4 input emission rate (lb/MMBtu) | eGRID subregion annual N2O input emission rate (lb/MMBtu) | eGRID subregion annual CO2 equivalent input emission rate (lb/MMBtu) | eGRID subregion annual Hg input emission rate (lb/MMBtu) | eGRID subregion annual NOx combustion output emission rate (lb/MWh) | eGRID subregion ozone season NOx combustion output emission rate (lb/MWh) | eGRID subregion annual SO2 combustion output emission rate (lb/MWh) | eGRID subregion annual CO2 combustion output emission rate (lb/MWh) | eGRID subregion annual CH4 combustion output emission rate (lb/MWh) | eGRID subregion annual N2O combustion output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent combustion output emission rate (lb/MWh) | eGRID subregion annual Hg combustion output emission rate (lb/MWh) | eGRID subregion annual NOx coal output emission rate (lb/MWh) | eGRID subregion annual NOx oil output emission rate (lb/MWh) | eGRID subregion annual NOx gas output emission rate (lb/MWh) | eGRID subregion annual NOx fossil fuel output emission rate (lb/MWh) | eGRID subregion ozone season NOx coal output emission rate (lb/MWh) | eGRID subregion ozone season NOx oil output emission rate (lb/MWh) | eGRID subregion ozone season NOx gas output emission rate (lb/MWh) | eGRID subregion ozone season NOx fossil fuel output emission rate (lb/MWh) | eGRID subregion annual SO2 coal output emission rate (lb/MWh) | eGRID subregion annual SO2 oil output emission rate (lb/MWh) | eGRID subregion annual SO2 gas output emission rate (lb/MWh) | eGRID subregion annual SO2 fossil fuel output emission rate (lb/MWh) | eGRID subregion annual CO2 coal output emission rate (lb/MWh) | eGRID subregion annual CO2 oil output emission rate (lb/MWh) | eGRID subregion annual CO2 gas output emission rate (lb/MWh) | eGRID subregion annual CO2 fossil fuel output emission rate (lb/MWh) | eGRID subregion annual CH4 coal output emission rate (lb/MWh) | eGRID subregion annual CH4 oil output emission rate (lb/MWh) | eGRID subregion annual CH4 gas output emission rate (lb/MWh) | eGRID subregion annual CH4 fossil fuel output emission rate (lb/MWh) | eGRID subregion annual N2O coal output emission rate (lb/MWh) | eGRID subregion annual N2O oil output emission rate (lb/MWh) | eGRID subregion annual N2O gas output emission rate (lb/MWh) | eGRID subregion annual N2O fossil fuel output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent coal output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent oil output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent gas output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent fossil fuel output emission rate (lb/MWh) | eGRID subregion annual Hg coal output emission rate (lb/MWh) | eGRID subregion annual Hg fossil fuel output emission rate (lb/MWh) | eGRID subregion annual NOx coal input emission rate (lb/MMBtu) | eGRID subregion annual NOx oil input emission rate (lb/MMBtu) | eGRID subregion annual NOx gas input emission rate (lb/MMBtu) | eGRID subregion annual NOx fossil fuel input emission rate (lb/MMBtu) | eGRID subregion ozone season NOx coal input emission rate (lb/MMBtu) | eGRID subregion ozone season NOx oil input emission rate (lb/MMBtu) | eGRID subregion ozone season NOx gas input emission rate (lb/MMBtu) | eGRID subregion ozone season NOx fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual SO2 coal input emission rate (lb/MMBtu) | eGRID subregion annual SO2 oil input emission rate (lb/MMBtu) | eGRID subregion annual SO2 gas input emission rate (lb/MMBtu) | eGRID subregion annual SO2 fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual CO2 coal input emission rate (lb/MMBtu) | eGRID subregion annual CO2 oil input emission rate (lb/MMBtu) | eGRID subregion annual CO2 gas input emission rate (lb/MMBtu) | eGRID subregion annual CO2 fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual CH4 coal input emission rate (lb/MMBtu) | eGRID subregion annual CH4 oil input emission rate (lb/MMBtu) | eGRID subregion annual CH4 gas input emission rate (lb/MMBtu) | eGRID subregion annual CH4 fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual N2O coal input emission rate (lb/MMBtu) | eGRID subregion annual N2O oil input emission rate (lb/MMBtu) | eGRID subregion annual N2O gas input emission rate (lb/MMBtu) | eGRID subregion annual N2O fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual CO2 equivalent coal input emission rate (lb/MMBtu) | eGRID subregion annual CO2 equivalent oil input emission rate (lb/MMBtu) | eGRID subregion annual CO2 equivalent gas input emission rate (lb/MMBtu) | eGRID subregion annual CO2 equivalent fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual Hg coal input emission rate (lb/MMBtu) | eGRID subregion annual Hg fossil fuel input emission rate (lb/MMBtu) | eGRID subregion annual NOx non-baseload output emission rate (lb/MWh) | eGRID subregion ozone season NOx non-baseload output emission rate (lb/MWh) | eGRID subregion annual SO2 non-baseload output emission rate (lb/MWh) | eGRID subregion annual CO2 non-baseload output emission rate (lb/MWh) | eGRID subregion annual CH4 non-baseload output emission rate (lb/MWh) | eGRID subregion annual N2O non-baseload output emission rate (lb/MWh) | eGRID subregion annual CO2e non-baseload output emission rate (lb/MWh) | eGRID subregion annual Hg non-baseload output emission rate (lb/MWh) | eGRID subregion annual coal net generation (MWh) | eGRID subregion annual oil net generation (MWh) | eGRID subregion annual gas net generation (MWh) | eGRID subregion annual nuclear net generation (MWh) | eGRID subregion annual hydro net generation (MWh) | eGRID subregion annual biomass net generation (MWh) | eGRID subregion annual wind net generation (MWh) | eGRID subregion annual solar net generation (MWh) | eGRID subregion annual geothermal net generation (MWh) | eGRID subregion annual other fossil net generation (MWh) | eGRID subregion annual other unknown/ purchased fuel net generation (MWh) | eGRID subregion annual total nonrenewables net generation (MWh) | eGRID subregion annual total renewables net generation (MWh) | eGRID subregion annual total nonhydro renewables net generation (MWh) | eGRID subregion annual total combustion net generation (MWh) | eGRID subregion annual total noncombustion net generation (MWh) | eGRID subregion coal generation percent (resource mix) | eGRID subregion oil generation percent (resource mix) | eGRID subregion gas generation percent (resource mix) | eGRID subregion nuclear generation percent (resource mix) | eGRID subregion hydro generation percent (resource mix) | eGRID subregion biomass generation percent (resource mix) | eGRID subregion wind generation percent (resource mix) | eGRID subregion solar generation percent (resource mix) | eGRID subregion geothermal generation percent (resource mix) | eGRID subregion other fossil generation percent (resource mix) | eGRID subregion other unknown/ purchased fuel generation percent (resource mix) | eGRID subregion total nonrenewables generation percent (resource mix) | eGRID subregion total renewables generation percent (resource mix) | eGRID subregion total nonhydro renewables generation percent (resource mix) | eGRID subregion total combustion generation percent (resource mix) | eGRID subregion total noncombustion generation percent (resource mix) | eGRID subregion annual nonbaseload coal net generation (MWh) | eGRID subregion annual nonbaseload oil net generation (MWh) | eGRID subregion annual nonbaseload gas net generation (MWh) | eGRID subregion annual nonbaseload nuclear net generation (MWh) | eGRID subregion annual nonbaseload hydro net generation (MWh) | eGRID subregion annual nonbaseload biomass net generation (MWh) | eGRID subregion annual nonbaseload wind net generation (MWh) | eGRID subregion annual nonbaseload solar net generation (MWh) | eGRID subregion annual nonbaseload geothermal net generation (MWh) | eGRID subregion annual nonbaseload other fossil net generation (MWh) | eGRID subregion annual nonbaseload other unknown/ purchased fuel net generation (MWh) | eGRID subregion nonbaseload coal generation percent (resource mix) | eGRID subregion nonbaseload oil generation percent (resource mix) | eGRID subregion nonbaseload gas generation percent (resource mix) | eGRID subregion nonbaseload nuclear generation percent (resource mix) | eGRID subregion nonbaseload hydro generation percent (resource mix) | eGRID subregion nonbaseload biomass generation percent (resource mix) | eGRID subregion nonbaseload wind generation percent (resource mix) | eGRID subregion nonbaseload solar generation percent (resource mix) | eGRID subregion nonbaseload geothermal generation percent (resource mix) | eGRID subregion nonbaseload other fossil generation percent (resource mix) | eGRID subregion nonbaseload other unknown/ purchased fuel generation percent (resource mix)
|  |  |  | SRNAMEPCAP | STHTIAN | STHTIOZ | STNGENAN | STNGENOZ | STNOXAN | STNOXOZ | STSO2AN | STCO2AN | STCH4AN | STN2OAN | STCO2EQA | STHGAN | STNOXRTA | STNOXRTO | STSO2RTA | STCO2RTA | STCH4RTA | STN2ORTA | STC2ERTA | STHGRTA | STNOXRA | STNOXRO | STSO2RA | STCO2RA | STHGRA | STNOXCRT | STNOXCRO | STSO2CRT | STCO2CRT | STCH4CRT | STN2OCRT | STHGCRT | STCNOXRT | STONOXRT | STGNOXRT | STFSNXRT | STCNXORT | STONXORT | STGNXORT | STFSNORT | STCSO2RT | STOSO2RT | STGSO2RT | STFSS2RT | STCCO2RT | STOCO2RT | STGCO2RT | STFSC2RT | STCHGRT | STFSHGRT | STCNOXR | STONOXR | STGNOXR | STFSNXR | STCNXOR | STONXOR | STGNXOR | STFSNOR | STCSO2R | STOSO2R | STGSO2R | STFSS2R | STCCO2R | STOCO2R | STGCO2R | STFSC2R | STCHGR | STFSHGR | STNBNOX | STNBNXO | STNBSO2 | STNBCO2 | STNBCH4 | STNBN2O | SRNBC2E | STNBHG | STGENACL | STGENAOL | STGENAGS | STGENANC | STGENAHY | STGENABM | STGENAWI | STGENASO | STGENAGT | STGENAOF | STGENAOP | STGENATN | STGENATR | STGENATH | STGENACY | STGENACN | STCLPR | STOLPR | STGSPR | STNCPR | STHYPR | STBMPR | STWIPR | STSOPR | STGTPR | STOFPR | STOPPR | STTNPR | STTRPR | STTHPR | STCYPR | STCNPR |  | STAHR
| SEQST99 State sequence number | PSTATABB State abbreviation | FIPST FIPS State code | State nameplate capacity (MW) | State annual heat input (MMBtu) | State ozone season heat input (MMBtu) | State annual net generation (MWh) | State ozone season net generation (MWh) | State annual NOx emissions (tons) | State ozone season NOx emissions (tons) | State annual SO2 emissions (tons) | State annual CO2 emissions (tons) | State annual CH4 emissions (lbs) | State annual N2O emissions (lbs) | State annual CO2 equivalent emissions (tons) | State annual Hg emissions (lbs) | State annual NOx total output emission rate (lb/MWh) | State ozone season NOx total output emission rate (lb/MWh) | State annual SO2 total output emission rate (lb/MWh) | State annual CO2 total output emission rate (lb/MWh) | State annual CH4 total output emission rate (lb/MWh) | State annual N2O total output emission rate (lb/MWh) | State annual CO2 equivalent total output emission rate (lb/MWh) | State annual Hg total output emission rate (lb/GWh) | State annual NOx input emission rate (lb/MMBtu) | State ozone season NOx input emission rate (lb/MMBtu) | State annual SO2 input emission rate (lb/MMBtu) | State annual CO2 input emission rate (lb/MMBtu) | State annual Hg input emission rate (lb/BBtu) | State annual NOx combustion output emission rate (lb/MWh) | State ozone season NOx combustion output emission rate (lb/MWh) | State annual SO2 combustion output emission rate (lb/MWh) | State annual CO2 combustion output emission rate (lb/MWh) | State annual CH4 combustion output emission rate (lb/MWh) | State annual N2O combustion output emission rate (lb/MWh) | State annual Hg combustion output emission rate (lb/GWh) | State annual NOx coal output emission rate (lb/MWh) | State annual NOx oil output emission rate (lb/MWh) | State annual NOx gas output emission rate (lb/MWh) | State annual NOx fossil fuel output emission rate (lb/MWh) | State ozone season NOx coal output emission rate (lb/MWh) | State ozone season NOx oil output emission rate (lb/MWh) | State ozone season NOx gas output emission rate (lb/MWh) | State ozone season NOx fossil fuel output emission rate (lb/MWh) | State annual SO2 coal output emission rate (lb/MWh) | State annual SO2 oil output emission rate (lb/MWh) | State annual SO2 gas output emission rate (lb/MWh) | State annual SO2 fossil fuel output emission rate (lb/MWh) | State annual CO2 coal output emission rate (lb/MWh) | State annual CO2 oil output emission rate (lb/MWh) | State annual CO2 gas output emission rate (lb/MWh) | State annual CO2 fossil fuel output emission rate (lb/MWh) | State annual Hg coal output emission rate (lb/GWh) | State annual Hg fossil fuel output emission rate (lb/GWh) | State annual NOx coal input emission rate (lb/MMBtu) | State annual NOx oil input emission rate (lb/MMBtu) | State annual NOx gas input emission rate (lb/MMBtu) | State annual NOx fossil fuel input emission rate (lb/MMBtu) | State ozone season NOx coal input emission rate (lb/MMBtu) | State ozone season NOx oil input emission rate (lb/MMBtu) | State ozone season NOx gas input emission rate (lb/MMBtu) | State ozone season NOx fossil fuel input emission rate (lb/MMBtu) | State annual SO2 coal input emission rate (lb/MMBtu) | State annual SO2 oil input emission rate (lb/MMBtu) | State annual SO2 gas input emission rate (lb/MMBtu) | State annual SO2 fossil fuel input emission rate (lb/MMBtu) | State annual CO2 coal input emission rate (lb/MMBtu) | State annual CO2 oil input emission rate (lb/MMBtu) | State annual CO2 gas input emission rate (lb/MMBtu) | State annual CO2 fossil fuel input emission rate (lb/MMBtu) | State annual Hg coal input emission rate (lb/BBtu) | State annual Hg fossil fuel input emission rate (lb/BBtu) | State annual NOx non-baseload output emission rate (lb/MWh) | State ozone season NOx non-baseload output emission rate (lb/MWh) | State annual SO2 non-baseload output emission rate (lb/MWh) | State annual CO2 non-baseload output emission rate (lb/MWh) | State annual CH4 non-baseload output emission rate (lb/MWh) | State annual N2O non-baseload output emission rate (lb/MWh) | eGRID subregion annual CO2 equivalent non-baseload output emission rate (lb/MWh) | State annual Hg non-baseload output emission rate (lb/GWh) | State annual coal net generation (MWh) | State annual oil net generation (MWh) | State annual gas net generation (MWh) | State annual nuclear net generation (MWh) | State annual hydro net generation (MWh) | State annual biomass net generation (MWh) | State annual wind net generation (MWh) | State annual solar net generation (MWh) | State annual geothermal net generation (MWh) | State annual other fossil net generation (MWh) | State annual other unknown/ purchased fuel net generation (MWh) | State annual total nonrenewables net generation (MWh) | State annual total renewables net generation (MWh) | State annual total nonhydro renewables net generation (MWh) | State annual total combustion net generation (MWh) | State annual total noncombustion net generation (MWh) | State coal generation percent (resource mix) | State oil generation percent (resource mix) | State gas generation percent (resource mix) | State nuclear generation percent (resource mix) | State hydro generation percent (resource mix) | State biomass generation percent (resource mix) | State wind generation percent (resource mix) | State solar generation percent (resource mix) | State geothermal generation percent (resource mix) | State other fossil generation percent (resource mix) | State other unknown/ purchased fuel generation percent (resource mix) | State total nonrenewables generation percent (resource mix) | State total renewables generation percent (resource mix) | State total nonhydro renewables generation percent (resource mix) | State total combustion generation percent (resource mix) | State total noncombustion generation percent (resource mix) |  | Total Annual Heat Rate (Btu/kWh) | Fossil Annual Heat Rate (Btu/kWh) | Non-Baseload Annual Heat Rate (Btu/kWh) | Coal Annual Heat Rate (Btu/kWh) | Oil Annual Heat Rate (Btu/kWh) | Natural Gas Annual Heat Rate (Btu/kWh) |  | Calculated Fossil CO2 - lb/MWh
16 | 1 | US Average |  | 1258286 | 22542508669.201 | 10780196178.726 | 4120144619.358 | 1866124658.226 | 1080607.792 | 489928.882 | 1094490.739 | 1755800221.732 | 291624356.759 | 41236029.87 | 1765520482.754 | -- | 0.525 | 0.525 | 0.531 | 852.3 | 0.071 | 0.01 | 857.019 | -- | 0.096 | 0.091 | 0.097 | 155.777 | -- | 0.836 | 0.836 | 0.846 | 1357.769 | 0.113 | 0.016 | -- | 1.327 | 4.961 | 0.414 | 0.805 | 1.246 | 4.558 | 0.413 | 0.772 | 2.003 | 6.265 | 0.021 | 0.837 | 2150.591 | 1666.586 | 893.7 | 1382.696 | -- | -- | 0.126 | 0.501 | 0.055 | 0.093 | 0.118 | 0.457 | 0.054 | 0.088 | 0.19 | 0.633 | 0.003 | 0.096 | 204.45 | 168.302 | 119.043 | 159.341 | -- | -- | 0.949 | 0.897 | 0.866 | 1410.007 | 0.11 | 0.016 | 1417.337 | -- | 900636364.662 | 26067180.125 | 1582553192.888 | 778187988 | 246429051.76 | 53540451.224 | 378266790.19 | 114984361.99 | 15974767 | 19315147.854 | 4189323.157 | 3310949196.686 | 809195422.164 | 562766370.404 | 2586301659.91 | 1533842958.94 | 21.86% | 0.6327% | 38.41% | 18.89% | 5.981% | 1.299% | 9.181% | 2.791% | 0.3877% | 0.4688% | 0.1017% | 80.36% | 19.64% | 13.66% | 62.77% | 37.23% |  | 5471.2906 | 8677.5908 | 8848.9905 | 10518.9093 | 9902.3541 | 7507.3713
17 | 63 | AKGD - ASCC Alaska Grid |  | 2123.9 | 36915776.633 | 14675641.997 | 4923739.78 | 1968662.519 | 13649.157 | 5873.268 | 927.668 | 2628489.691 | 450096.095 | 61195.668 | 2643234.046 | -- | 5.544 | 5.967 | 0.377 | 1067.68 | 0.091 | 0.012 | 1073.669 | -- | 0.739 | 0.8 | 0.05 | 142.405 | -- | 6.417 | 6.906 | 0.436 | 1235.69 | 0.106 | 0.014 | -- | 1.907 | 7.847 | 7.414 | 6.469 | 1.779 | 7.947 | 8.278 | 7.009 | 0.938 | 2.213 | 0.026 | 0.437 | 2274.583 | 1435.591 | 953.282 | 1245.833 | -- | -- | 0.178 | 0.919 | 0.909 | 0.748 | 0.169 | 0.915 | 1.014 | 0.809 | 0.088 | 0.259 | 0.003 | 0.05 | 212.862 | 168.214 | 116.889 | 143.953 | -- | -- | 6.604 | 7.173 | 0.524 | 1229.641 | 0.12 | 0.016 | 1237.515 | -- | 752894.449 | 482672.34 | 2984081.036 | 0 | 567393 | 38070.956 | 102061 | 0 | 0 | 0 | -3433 | 4216214.825 | 707524.956 | 140131.956 | 4254285.781 | 669454 | 15.29% | 9.803% | 60.61% | 0% | 11.52% | 0.7732% | 2.073% | 0% | 0% | 0% | 0% | 85.63% | 14.37% | 2.846% | 86.4% | 13.6% |  | 7497.5076 | 8654.4428 | 8541.9616 | 10685.7166 | 8534.3134 | 8155.4466
18 | 64 | AKMS - ASCC Miscellaneous |  | 919.9 | 5366566.184 | 2144532.226 | 1672077.993 | 683463.008 | 6381.461 | 2413.705 | 565.509 | 405634.646 | 41729.689 | 7098.103 | 407213.885 | -- | 7.633 | 7.063 | 0.676 | 485.186 | 0.025 | 0.004 | 487.075 | -- | 2.378 | 2.251 | 0.211 | 151.171 | -- | 24.524 | 22.694 | 2.173 | 1558.873 | 0.08 | 0.014 | -- | 0 | 28.625 | 4.73 | 24.203 | 0 | 28.306 | 4.73 | 23.133 | 0 | 2.621 | 0.046 | 2.144 | 0 | 1508.157 | 1687.766 | 1541.398 | -- | -- | 0 | 3.098 | 0.328 | 2.372 | 0 | 3.096 | 0.328 | 2.245 | 0 | 0.284 | 0.003 | 0.21 | 0 | 163.218 | 116.889 | 151.083 | -- | -- | 24.568 | 23.467 | 2.138 | 1531.318 | 0.066 | 0.012 | 1536.461 | -- | 0 | 419813.301 | 101314.979 | 0 | 1121507 | 0 | 30151 | 0 | 0 | 0 | -708 | 520420.28 | 1151658 | 30151 | 520420.28 | 1151658 | 0% | 25.11% | 6.059% | 0% | 67.07% | 0% | 1.803% | 0% | 0% | 0% | 0% | 31.12% | 68.88% | 1.803% | 31.12% | 68.88% |  | 3209.5191 | 10202.3259 | 10135.6076 | - | 9240.139 | 14439.049
19 | 88 | AZNM - WECC Southwest |  | 51066.6 | 931148054.454 | 468950211.898 | 167984970.143 | 81063461.416 | 38904.753 | 19226.577 | 10711.571 | 68844905.807 | 8701022.518 | 1203010.43 | 69132917.145 | -- | 0.463 | 0.474 | 0.128 | 819.656 | 0.052 | 0.007 | 823.085 | -- | 0.084 | 0.082 | 0.023 | 147.871 | -- | 0.733 | 0.751 | 0.202 | 1297.38 | 0.082 | 0.011 | -- | 1.581 | 17.452 | 0.418 | 0.728 | 1.563 | 17.6 | 0.427 | 0.705 | 0.736 | 6.097 | 0.006 | 0.201 | 2331.892 | 3237.548 | 921.202 | 1296.814 | -- | -- | 0.139 | 0.88 | 0.054 | 0.083 | 0.137 | 0.878 | 0.055 | 0.082 | 0.064 | 0.308 | 0.001 | 0.023 | 204.479 | 163.326 | 118.729 | 148.557 | -- | -- | 0.664 | 0.644 | 0.162 | 1227.625 | 0.067 | 0.009 | 1231.997 | -- | 26836891.44 | 87445.169 | 78594979.14 | 31629862 | 5683092 | 591773.517 | 8739947 | 10050113.31 | 5752841 | 269.098 | 17756 | 137167202.847 | 30817766.827 | 25134674.827 | 106129114.364 | 61855855.31 | 15.98% | 0.05206% | 46.79% | 18.83% | 3.383% | 0.3523% | 5.203% | 5.983% | 3.425% | 0.0001602% | 0.01057% | 81.65% | 18.35% | 14.96% | 63.18% | 36.82% |  | 5543.0438 | 8729.4035 | 8263.6631 | 11404.0659 | 19822.6124 | 7758.8626
20 | 85 | CAMX - WECC California |  | 89051.4 | 910487207.384 | 439901147.235 | 204553916.344 | 101534037.273 | 53165.384 | 25129.2 | 3841.668 | 54378369.528 | 6433505.492 | 821400.569 | 54575632.055 | -- | 0.52 | 0.495 | 0.038 | 531.678 | 0.031 | 0.004 | 533.606 | -- | 0.117 | 0.114 | 0.008 | 119.449 | -- | 0.949 | 0.903 | 0.069 | 970.144 | 0.057 | 0.007 | -- | 2.742 | 28.259 | 0.699 | 0.862 | 2.823 | 29.218 | 0.665 | 0.855 | 0.613 | 2.009 | 0.009 | 0.055 | 1972.586 | 1664.414 | 918.769 | 997.972 | -- | -- | 0.285 | 2.569 | 0.09 | 0.109 | 0.304 | 2.822 | 0.085 | 0.107 | 0.064 | 0.183 | 0.001 | 0.007 | 205.234 | 151.283 | 117.955 | 125.898 | -- | -- | 0.849 | 0.796 | 0.057 | 1047.515 | 0.049 | 0.006 | 1050.551 | -- | 7855351.769 | 93721.012 | 97166849.457 | 16477366 | 13437119.01 | 5041118.87 | 15792024.41 | 38578240.94 | 8165475 | 1538572.469 | 408076.8 | 123539937.507 | 81013978.23 | 67576859.22 | 112103690.377 | 92450225.36 | 3.84% | 0.04582% | 47.5% | 8.055% | 6.569% | 2.464% | 7.72% | 18.86% | 3.992% | 0.7522% | 0.1995% | 60.39% | 39.61% | 33.04% | 54.8% | 45.2% |  | 4451.0867 | 7926.8297 | 8320.3466 | 9611.3997 | 11001.9896 | 7789.1484
21 | 65 | ERCT - ERCOT All |  | 130411.4 | 2265447510.33 | 1160897225.885 | 421638207.945 | 200067305.783 | 99484.491 | 47461.145 | 123711.817 | 171512266.825 | 22927901.38 | 3195031.445 | 172274925.279 | -- | 0.472 | 0.474 | 0.587 | 813.552 | 0.054 | 0.008 | 817.169 | -- | 0.088 | 0.082 | 0.109 | 151.416 | -- | 0.726 | 0.73 | 0.903 | 1252.384 | 0.084 | 0.012 | -- | 1.109 | 3.909 | 0.586 | 0.727 | 1.083 | 3.874 | 0.535 | 0.678 | 3.172 | 9.809 | 0.007 | 0.903 | 2256.778 | 2155.877 | 869.878 | 1256.382 | -- | -- | 0.103 | 0.313 | 0.08 | 0.088 | 0.101 | 0.309 | 0.072 | 0.082 | 0.295 | 0.785 | 0.001 | 0.109 | 210.069 | 172.563 | 118.445 | 151.959 | -- | -- | 0.773 | 0.701 | 0.728 | 1177.373 | 0.065 | 0.009 | 1181.606 | -- | 74510144.05 | 261481.947 | 196134770.376 | 40211257 | 684520.26 | 773485.116 | 92100198.55 | 14744933 | 0 | 1799765.717 | 417652 | 313335071.09 | 108303136.926 | 107618616.666 | 273897299.206 | 147740908.81 | 17.67% | 0.06202% | 46.52% | 9.537% | 0.1623% | 0.1834% | 21.84% | 3.497% | 0% | 0.4269% | 0.09905% | 74.31% | 25.69% | 25.52% | 64.96% | 35.04% |  | 5372.9654 | 8267.9012 | 7747.9649 | 10743.0321 | 12493.2749 | 7344.1513
22 | 66 | FRCC - FRCC All |  | 67680.2 | 1536122344.136 | 744049143.708 | 237351633.8 | 113592303.52 | 33902.753 | 15549.307 | 19854.482 | 98847877.315 | 12635070.019 | 1656407.722 | 99252620.438 | -- | 0.286 | 0.274 | 0.167 | 832.924 | 0.053 | 0.007 | 836.334 | -- | 0.044 | 0.042 | 0.026 | 128.698 | -- | 0.338 | 0.324 | 0.198 | 986.528 | 0.063 | 0.008 | -- | 0.513 | 10.492 | 0.182 | 0.241 | 0.485 | 10.424 | 0.181 | 0.234 | 0.81 | 2.102 | 0.043 | 0.177 | 1585.258 | 1549.255 | 858.938 | 986.226 | -- | -- | 0.055 | 1.104 | 0.026 | 0.032 | 0.052 | 1.251 | 0.025 | 0.031 | 0.087 | 0.221 | 0.006 | 0.024 | 170.389 | 163.044 | 120.411 | 131.256 | -- | -- | 0.354 | 0.339 | 0.204 | 1016.511 | 0.054 | 0.007 | 1019.969 | -- | 18374988.384 | 1155056.451 | 174502495.378 | 28058287 | 251607 | 3666177.294 | 0 | 8646287 | 0 | 1633386.359 | 1063348.853 | 224787562.425 | 12564071.294 | 12312464.294 | 200395452.719 | 36956181 | 7.742% | 0.4866% | 73.52% | 11.82% | 0.106% | 1.545% | 0% | 3.643% | 0% | 0.6882% | 0.448% | 94.71% | 5.293% | 5.187% | 84.43% | 15.57% |  | 6471.9266 | 7513.7594 | 7744.4917 | 9303.7579 | 9502.0669 | 7133.3848
23 | 67 | HIMS - HICC Miscellaneous |  | 1045.2 | 18937391.314 | 7730992.167 | 2616354.001 | 1123051.876 | 9389.805 | 3929.735 | 3893.693 | 1483984.387 | 353826.663 | 53840.526 | 1496429.459 | -- | 7.178 | 6.998 | 2.976 | 1134.391 | 0.135 | 0.021 | 1143.904 | -- | 0.992 | 1.017 | 0.411 | 156.725 | -- | 10.57 | 10.306 | 4.383 | 1670.472 | 0.199 | 0.03 | -- | 0 | 10.787 | 0 | 10.787 | 0 | 10.618 | 0 | 10.618 | 0 | 4.488 | 0 | 4.488 | 0 | 1690.098 | 0 | 1690.098 | -- | -- | 0 | 1.025 | 0 | 1.025 | 0 | 1.011 | 0 | 1.011 | 0 | 0.427 | 0 | 0.427 | 0 | 160.617 | 0 | 160.617 | -- | -- | 11.266 | 11.077 | 4.199 | 1649.353 | 0.176 | 0.027 | 1661.915 | -- | 0 | 1683592.267 | 0 | 0 | 114971 | 95913.734 | 386781 | 154486 | 183391 | 0 | -2781 | 1680811.267 | 935542.734 | 820571.734 | 1776725.001 | 839629 | 0% | 64.35% | 0% | 0% | 4.394% | 3.666% | 14.78% | 5.905% | 7.009% | 0% | 0% | 64.24% | 35.76% | 31.36% | 67.91% | 32.09% |  | 7238.0845 | 10522.535 | 10268.857 | - | 10522.535 | -
24 | 68 | HIOA - HICC Oahu |  | 2220 | 64330749.494 | 27486168.328 | 6564236.001 | 2850279.003 | 12867.179 | 5541.166 | 21439.55 | 5360015.667 | 1156250.468 | 176265.667 | 5400732.382 | -- | 3.92 | 3.888 | 6.532 | 1633.097 | 0.176 | 0.027 | 1645.502 | -- | 0.4 | 0.403 | 0.667 | 166.639 | -- | 4.331 | 4.296 | 7.217 | 1804.227 | 0.195 | 0.03 | -- | 2.825 | 4.534 | 0 | 4.193 | 2.779 | 4.579 | 0 | 4.217 | 5.228 | 8.318 | 0 | 7.702 | 2393.72 | 1638.066 | 0 | 1788.702 | -- | -- | 0.252 | 0.452 | 0 | 0.409 | 0.249 | 0.46 | 0 | 0.413 | 0.467 | 0.829 | 0 | 0.751 | 213.892 | 163.316 | 0 | 174.311 | -- | -- | 4.472 | 4.451 | 7.796 | 1784.006 | 0.172 | 0.027 | 1796.311 | -- | 1084555.1 | 4471615.153 | 0 | 0 | 0 | 186723.71 | 271110 | 351508 | 0 | 198724.533 | 0 | 5754894.786 | 809341.71 | 809341.71 | 5941618.496 | 622618 | 16.52% | 68.12% | 0% | 0% | 0% | 2.845% | 4.13% | 5.355% | 0% | 3.027% | 0% | 87.67% | 12.33% | 12.33% | 90.51% | 9.485% |  | 9800.1884 | 10261.5555 | 10234.6151 | 11191.2554 | 10030.0399 | -
25 | 69 | MROE - MRO East |  | 8177.7 | 219619275.486 | 112466698.224 | 24114780.661 | 11484133.545 | 11089.459 | 5723.459 | 4736.46 | 19076415.713 | 3573181.104 | 520813.499 | 19198681.686 | -- | 0.92 | 0.997 | 0.393 | 1582.135 | 0.148 | 0.022 | 1592.275 | -- | 0.101 | 0.102 | 0.043 | 173.723 | -- | 1.013 | 1.098 | 0.433 | 1743.317 | 0.163 | 0.024 | -- | 0.761 | 1.019 | 1.341 | 0.976 | 0.79 | 0.992 | 1.501 | 1.046 | 0.506 | 2.31 | 0.071 | 0.367 | 2198.654 | 1564.183 | 1167.079 | 1814.125 | -- | -- | 0.072 | 0.102 | 0.137 | 0.095 | 0.074 | 0.098 | 0.136 | 0.097 | 0.048 | 0.23 | 0.007 | 0.036 | 209.481 | 155.94 | 119.621 | 177.507 | -- | -- | 1.161 | 1.237 | 0.37 | 1555.943 | 0.133 | 0.019 | 1565.03 | -- | 13113744.762 | 277669.969 | 7752645.667 | 0 | 1179385.83 | 725508.414 | 748679 | 301525 | 0 | 15622.902 | 0 | 21159683.3 | 2955098.244 | 1775712.414 | 21885191.714 | 2229589.83 | 54.38% | 1.151% | 32.15% | 0% | 4.891% | 3.009% | 3.105% | 1.25% | 0% | 0.06479% | 0% | 87.75% | 12.25% | 7.364% | 90.75% | 9.246% |  | 9107.2475 | 10220.0195 | 8765.5304 | 10495.7204 | 10030.6721 | 9756.4725
26 | 70 | MROW - MRO West |  | 75973 | 1250354416.892 | 598639763.439 | 242821306.178 | 104662080.908 | 91542.06 | 42994.03 | 119064.654 | 120899511.387 | 25992944.009 | 3757128.096 | 121781406.386 | -- | 0.754 | 0.822 | 0.981 | 995.79 | 0.107 | 0.015 | 1003.054 | -- | 0.146 | 0.144 | 0.19 | 193.384 | -- | 1.464 | 1.596 | 1.905 | 1934.159 | 0.208 | 0.03 | -- | 1.659 | 7.392 | 0.521 | 1.438 | 1.645 | 4.967 | 0.492 | 1.407 | 2.414 | 1.087 | 0.02 | 1.919 | 2226.49 | 1093.232 | 962.897 | 1964.276 | -- | -- | 0.157 | 0.965 | 0.064 | 0.143 | 0.157 | 0.888 | 0.06 | 0.141 | 0.229 | 0.142 | 0.002 | 0.191 | 211.408 | 142.744 | 118.431 | 195.806 | -- | -- | 1.43 | 1.381 | 1.715 | 1808.282 | 0.183 | 0.026 | 1820.619 | -- | 96229385.883 | 419423.735 | 25828070.282 | 21003393 | 10624696.59 | 1826504.727 | 83948227 | 2229935.21 | 0 | 327106.867 | 384563.609 | 144191943.376 | 98629363.527 | 88004666.937 | 125015055.103 | 117806251.8 | 39.63% | 0.1727% | 10.64% | 8.65% | 4.376% | 0.7522% | 34.57% | 0.9183% | 0% | 0.1347% | 0.1584% | 59.38% | 40.62% | 36.24% | 51.48% | 48.52% |  | 5149.278 | 10031.7457 | 9235.0694 | 10531.7207 | 7658.6897 | 8130.4473
27 | 72 | NEWE - NPCC New England |  | 39851.7 | 508980792.765 | 235605421.954 | 103068943.759 | 46193026.563 | 16864.693 | 7300.261 | 4824.797 | 27796015.525 | 7470000.348 | 971798.627 | 28034171.965 | -- | 0.327 | 0.316 | 0.094 | 539.367 | 0.072 | 0.009 | 543.989 | -- | 0.066 | 0.062 | 0.019 | 109.222 | -- | 0.528 | 0.51 | 0.151 | 869.739 | 0.117 | 0.015 | -- | 2.535 | 5.84 | 0.203 | 0.231 | 3.68 | 4.098 | 0.199 | 0.22 | 1.387 | 3.067 | 0.02 | 0.035 | 2293.733 | 2204.392 | 848.838 | 859.914 | -- | -- | 0.227 | 0.383 | 0.029 | 0.032 | 0.271 | 0.255 | 0.028 | 0.031 | 0.124 | 0.201 | 0.003 | 0.005 | 204.931 | 144.532 | 119.551 | 120.375 | -- | -- | 0.411 | 0.361 | 0.13 | 900.489 | 0.073 | 0.009 | 905.118 | -- | 578806.817 | 243492.662 | 55950673.629 | 27072626 | 5840245.56 | 5328618.766 | 3780159.25 | 2457857.32 | 0 | 1720733.702 | 95729 | 85662061.81 | 17406880.896 | 11566635.336 | 63918054.576 | 39150888.13 | 0.5616% | 0.2362% | 54.28% | 26.27% | 5.666% | 5.17% | 3.668% | 2.385% | 0% | 1.669% | 0.09288% | 83.11% | 16.89% | 11.22% | 62.01% | 37.99% |  | 4938.2556 | 7143.6262 | 7480.6978 | 11192.7088 | 15251.9304 | 7100.2166
28 | 86 | NWPP - WECC Northwest |  | 79135.5 | 1089360733.767 | 486028811.707 | 282815849.052 | 119082556.506 | 78144.677 | 34738.609 | 48492.349 | 89737301.175 | 16429445.174 | 2346387.865 | 90292280.965 | -- | 0.553 | 0.583 | 0.343 | 634.599 | 0.058 | 0.008 | 638.523 | -- | 0.143 | 0.143 | 0.089 | 164.752 | -- | 1.324 | 1.398 | 0.822 | 1520.475 | 0.139 | 0.02 | -- | 1.983 | 1.59 | 0.676 | 1.301 | 1.985 | 1.488 | 0.692 | 1.316 | 1.555 | 16.639 | 0.009 | 0.81 | 2283.222 | 1822.716 | 908.592 | 1565.218 | -- | -- | 0.18 | 0.196 | 0.088 | 0.141 | 0.179 | 0.186 | 0.089 | 0.14 | 0.141 | 2.056 | 0.001 | 0.088 | 207.286 | 225.242 | 118.685 | 169.162 | -- | -- | 1.526 | 1.513 | 0.758 | 1545.746 | 0.139 | 0.02 | 1555.177 | -- | 53734880.77 | 532249.04 | 59582309.499 | 8511288 | 115371498.39 | 3164871.176 | 32482354 | 6539173.82 | 1873060 | 717708.37 | 306455.744 | 123384891.423 | 159430957.386 | 44059458.996 | 118038474.599 | 164777374.21 | 19% | 0.1882% | 21.07% | 3.009% | 40.79% | 1.119% | 11.49% | 2.312% | 0.6623% | 0.2538% | 0.1084% | 43.63% | 56.37% | 15.58% | 41.74% | 58.26% |  | 3851.8376 | 9252.7754 | 9137.6669 | 11014.8394 | 8092.2563 | 7655.4914
29 | 73 | NYCW - NPCC NYC/Westchester |  | 14076.4 | 223387774.961 | 112952776.536 | 32499681.01 | 14553976.178 | 3673.759 | 1935.344 | 172.756 | 13272151.169 | 630509.353 | 69932.847 | 13290452.528 | -- | 0.226 | 0.266 | 0.011 | 816.756 | 0.019 | 0.002 | 817.882 | -- | 0.033 | 0.034 | 0.002 | 118.826 | -- | 0.248 | 0.291 | 0.012 | 894.735 | 0.021 | 0.002 | -- | 0 | 10.206 | 0.216 | 0.223 | 0 | 11.508 | 0.238 | 0.243 | 0 | 1.27 | 0.007 | 0.008 | 0 | 2144.514 | 892.967 | 893.789 | -- | -- | 0 | 0.613 | 0.029 | 0.03 | 0 | 0.401 | 0.031 | 0.031 | 0 | 0.076 | 0.001 | 0.001 | 0 | 128.732 | 118.927 | 118.942 | -- | -- | 0.309 | 0.333 | 0.011 | 930.849 | 0.02 | 0.002 | 932 | -- | 0 | 65083.006 | 29278907.538 | 2821401 | 0 | 145417.12 | 0 | 11057 | 0 | 177734.89 | 80 | 32343206.434 | 156474.12 | 156474.12 | 29667222.554 | 2832458 | 0% | 0.2003% | 90.09% | 8.681% | 0% | 0.4474% | 0% | 0.03402% | 0% | 0.5469% | 0.0002462% | 99.52% | 0.4815% | 0.4815% | 91.28% | 8.715% |  | 6873.5375 | 7514.4945 | 7826.0749 | - | 16658.7484 | 7508.5304
30 | 71 | NYLI - NPCC Long Island |  | 5867.5 | 120510033.559 | 61366014.421 | 11938038.027 | 5990556.138 | 5443.718 | 2772.817 | 1576.469 | 7228120.924 | 1502288.529 | 193417.387 | 7275718.722 | -- | 0.912 | 0.926 | 0.264 | 1210.94 | 0.126 | 0.016 | 1218.914 | -- | 0.09 | 0.09 | 0.026 | 119.959 | -- | 0.928 | 0.942 | 0.269 | 1232.774 | 0.128 | 0.016 | -- | 0 | 4.606 | 0.599 | 0.653 | 0 | 6.422 | 0.623 | 0.699 | 0 | 0.461 | 0.232 | 0.235 | 0 | 2071.184 | 1146.285 | 1158.625 | -- | -- | 0 | 0.361 | 0.063 | 0.069 | 0 | 0.347 | 0.064 | 0.071 | 0 | 0.036 | 0.024 | 0.025 | 0 | 162.212 | 120.929 | 121.668 | -- | -- | 0.893 | 0.909 | 0.324 | 1317.314 | 0.04 | 0.005 | 1319.797 | -- | 0 | 603902.864 | 10191948.616 | 0 | 0 | 419316.339 | 0 | 211444 | 0 | 512502.295 | -1076 | 11307277.775 | 630760.339 | 630760.339 | 11726594.114 | 211444 | 0% | 5.059% | 85.37% | 0% | 0% | 3.512% | 0% | 1.771% | 0% | 4.293% | 0% | 94.72% | 5.284% | 5.284% | 98.23% | 1.771% |  | 10094.6264 | 9522.8408 | 10827.1197 | - | 12768.3772 | 9478.9918 |  | 1905.2407
31 | 74 | NYUP - NPCC Upstate NY |  | 25578.1 | 182150908.41 | 85229287.981 | 85506174.471 | 36644959.257 | 4290.829 | 1960.111 | 628.354 | 9964947.042 | 1302743.539 | 161797.025 | 10005339.093 | -- | 0.1 | 0.107 | 0.015 | 233.081 | 0.015 | 0.002 | 234.026 | -- | 0.047 | 0.046 | 0.007 | 109.414 | -- | 0.36 | 0.384 | 0.053 | 836.821 | 0.055 | 0.007 | -- | 0 | 2.132 | 0.211 | 0.242 | 0 | 2.017 | 0.206 | 0.239 | 0 | 0.84 | 0.014 | 0.027 | 0 | 865.639 | 850.157 | 850.408 | -- | -- | 0 | 0.257 | 0.029 | 0.034 | 0 | 0.215 | 0.028 | 0.033 | 0 | 0.101 | 0.002 | 0.004 | 0 | 104.435 | 118.444 | 118.183 | -- | -- | 0.439 | 0.431 | 0.062 | 880.743 | 0.047 | 0.006 | 883.603 | -- | 0 | 31618.158 | 22172593.339 | 28355182 | 28374339 | 1338577.413 | 4156369 | 804077 | 0 | 285455.338 | -12037 | 50832811.835 | 34673362.413 | 6299023.413 | 23816207.248 | 61689967 | 0% | 0.03698% | 25.93% | 33.16% | 33.18% | 1.565% | 4.861% | 0.9404% | 0% | 0.3338% | 0% | 59.45% | 40.55% | 7.367% | 27.85% | 72.15% |  | 2130.2661 | 7195.688 | 7452.3662 | - | 8288.7825 | 7177.7127 |  | 1695.0753
32 | 75 | RFCE - RFC East |  | 79307 | 1409304227.47 | 650512973.375 | 290415250.316 | 129236298.239 | 42971.73 | 18855.907 | 48959.531 | 97693765.556 | 14309163.641 | 1926849.057 | 98159730.616 | -- | 0.296 | 0.292 | 0.337 | 672.787 | 0.049 | 0.007 | 675.996 | -- | 0.061 | 0.058 | 0.069 | 138.641 | -- | 0.487 | 0.48 | 0.555 | 1106.993 | 0.081 | 0.011 | -- | 1.422 | 5.277 | 0.173 | 0.419 | 1.359 | 3.716 | 0.163 | 0.407 | 2.92 | 0.369 | 0.013 | 0.536 | 2233.932 | 1597.944 | 851.997 | 1103.007 | -- | -- | 0.131 | 0.408 | 0.024 | 0.054 | 0.126 | 0.288 | 0.023 | 0.052 | 0.269 | 0.029 | 0.002 | 0.069 | 206.154 | 123.662 | 119.548 | 141.099 | -- | -- | 0.838 | 0.76 | 0.955 | 1357.299 | 0.106 | 0.015 | 1364.366 | -- | 29968363.265 | 229947.18 | 141430694.976 | 104656850 | 4084335 | 2768180.935 | 2887662 | 2283423.2 | 0 | 2111491.116 | -5700 | 278391646.537 | 12023601.135 | 7939266.135 | 176502977.472 | 113912270.2 | 10.32% | 0.07918% | 48.7% | 36.04% | 1.406% | 0.9532% | 0.9943% | 0.7863% | 0% | 0.7271% | 0% | 95.86% | 4.14% | 2.734% | 60.78% | 39.22% |  | 4852.7211 | 7817.256 | 9619.4799 | 10836.2292 | 12921.8677 | 7126.8194 |  | 969.4014
33 | 76 | RFCM - RFC Michigan |  | 29832.6 | 669319419.371 | 301127107.956 | 94434453.761 | 40171986.693 | 33690.954 | 14680.485 | 54038.381 | 57324576.651 | 10880447.448 | 1552375.908 | 57691886.253 | -- | 0.714 | 0.731 | 1.144 | 1214.061 | 0.115 | 0.016 | 1221.84 | -- | 0.101 | 0.098 | 0.161 | 171.292 | -- | 0.958 | 0.982 | 1.537 | 1630.8 | 0.155 | 0.022 | -- | 1.259 | 12.382 | 0.448 | 0.932 | 1.243 | 12.78 | 0.44 | 0.921 | 2.73 | 1.99 | 0.046 | 1.557 | 2239.212 | 1735.391 | 910.407 | 1658.276 | -- | -- | 0.117 | 1.43 | 0.058 | 0.099 | 0.115 | 1.493 | 0.055 | 0.096 | 0.254 | 0.23 | 0.006 | 0.166 | 208.512 | 200.473 | 118.273 | 176.281 | -- | -- | 1.079 | 1.07 | 1.816 | 1717.019 | 0.16 | 0.023 | 1727.848 | -- | 37052568.096 | 1140612.55 | 29382461.173 | 16384335 | -261038 | 1422695.716 | 7629388 | 379374 | 0 | 1304140.137 | -83 | 85264033.956 | 9170419.716 | 9431457.716 | 70302394.672 | 24132059 | 39.13% | 1.205% | 31.03% | 17.3% | 0% | 1.502% | 8.057% | 0.4006% | 0% | 1.377% | 0% | 90.29% | 9.711% | 9.96% | 74.45% | 25.55% |  | 7087.6613 | 9407.0036 | 9740.2386 | 10739.0078 | 8656.4824 | 7697.5049 |  | 1222.0127
34 | 77 | RFCW - RFC West |  | 138789.7 | 3128162475.068 | 1476385836.067 | 521426349.759 | 230451464.253 | 149082.229 | 60919.684 | 177388.183 | 272740309.949 | 49372302.411 | 7086179.31 | 274411838.705 | -- | 0.572 | 0.529 | 0.68 | 1046.132 | 0.095 | 0.014 | 1052.543 | -- | 0.095 | 0.083 | 0.113 | 174.377 | -- | 0.881 | 0.814 | 1.048 | 1611.246 | 0.146 | 0.021 | -- | 1.246 | 1.505 | 0.353 | 0.868 | 1.019 | 1.388 | 0.387 | 0.775 | 1.815 | 3.518 | 0.021 | 1.057 | 2158.192 | 2476.516 | 904.661 | 1629.869 | -- | -- | 0.119 | 0.115 | 0.046 | 0.094 | 0.097 | 0.107 | 0.049 | 0.082 | 0.173 | 0.268 | 0.003 | 0.114 | 206.203 | 188.754 | 118.628 | 176.018 | -- | -- | 1.055 | 0.955 | 1.128 | 1798.831 | 0.172 | 0.025 | 1810.499 | -- | 185455630.354 | 1497490.005 | 144627913.238 | 148434331 | 5655220.12 | 2637129.424 | 26977478.83 | 1813492.2 | 0 | 3901786.715 | 425879.946 | 484343031.258 | 37083320.574 | 31428100.454 | 338545829.682 | 182880522.15 | 35.57% | 0.2872% | 27.74% | 28.47% | 1.085% | 0.5058% | 5.174% | 0.3478% | 0% | 0.7483% | 0.08168% | 92.89% | 7.112% | 6.027% | 64.93% | 35.07% |  | 5999.2413 | 9259.6723 | 10219.5855 | 10466.3463 | 13120.3365 | 7626.0326 |  | 989.5556
35 | 87 | RMPA - WECC Rockies |  | 23374 | 425286051.512 | 192532118.917 | 66044054.33 | 29000429.671 | 20067.966 | 8572.524 | 11353.271 | 38267891.985 | 7185952.89 | 1030736.854 | 38511296.163 | -- | 0.608 | 0.591 | 0.344 | 1158.86 | 0.109 | 0.016 | 1166.231 | -- | 0.094 | 0.089 | 0.053 | 179.963 | -- | 0.965 | 0.938 | 0.546 | 1839.465 | 0.173 | 0.025 | -- | 1.225 | 22.788 | 0.471 | 0.961 | 1.158 | 23.908 | 0.474 | 0.897 | 0.843 | 4.304 | 0.018 | 0.548 | 2284.523 | 2324.594 | 1071.104 | 1849.435 | -- | -- | 0.111 | 1.601 | 0.053 | 0.094 | 0.106 | 1.615 | 0.054 | 0.089 | 0.077 | 0.302 | 0.002 | 0.054 | 207.645 | 163.326 | 121.134 | 180.812 | -- | -- | 0.859 | 0.807 | 0.402 | 1614.205 | 0.128 | 0.018 | 1622.804 | -- | 26212803.59 | 27853.383 | 15136584.033 | 0 | 6218312 | 169082.422 | 16494058 | 1724050.95 | 0 | 6452 | 54858 | 41438551.006 | 24605503.372 | 18387191.372 | 41607633.428 | 24436420.95 | 39.69% | 0.04217% | 22.92% | 0% | 9.415% | 0.256% | 24.97% | 2.61% | 0% | 0.009769% | 0.08306% | 62.74% | 37.26% | 27.84% | 63% | 37% |  | 6439.4298 | 10228.497 | 8927.5325 | 11002.0612 | 14232.8472 | 8842.3069 |  | 1742.7478
36 | 83 | SPNO - SPP North |  | 26827.8 | 374325907.373 | 189646670.123 | 73370170.814 | 33162072.291 | 19938.793 | 9277.761 | 6381.551 | 36381644.853 | 7929750.669 | 1148887.594 | 36651950.989 | -- | 0.544 | 0.56 | 0.174 | 991.729 | 0.108 | 0.016 | 999.097 | -- | 0.107 | 0.098 | 0.034 | 194.385 | -- | 1.073 | 1.105 | 0.343 | 1957.831 | 0.213 | 0.031 | -- | 0.969 | 29.259 | 1.332 | 1.075 | 0.961 | 25.968 | 0.988 | 0.982 | 0.401 | 2.127 | 0.074 | 0.343 | 2170.873 | 3263.583 | 1019.482 | 1961.541 | -- | -- | 0.093 | 1.46 | 0.156 | 0.107 | 0.093 | 1.656 | 0.119 | 0.098 | 0.039 | 0.106 | 0.009 | 0.034 | 208.78 | 162.864 | 119.523 | 194.806 | -- | -- | 1.192 | 1.042 | 0.35 | 1926.223 | 0.204 | 0.029 | 1940.098 | -- | 29795057.941 | 313592.527 | 6981816.526 | 8574732 | 151476 | 69803 | 27379680 | 99035 | 0 | 0 | 4978 | 45670176.994 | 27699994 | 27548518 | 37165247.994 | 36204923 | 40.61% | 0.4274% | 9.516% | 11.69% | 0.2065% | 0.09514% | 37.32% | 0.135% | 0% | 0% | 0.006785% | 62.25% | 37.75% | 37.55% | 50.65% | 49.35% |  | 5101.8814 | 10069.2022 | 9887.9039 | 10397.8973 | 20038.701 | 8529.5884 |  | 1592.9153
37 | 84 | SPSO - SPP South |  | 56227.5 | 936855526.17 | 479824960.886 | 148803952.984 | 69497335.268 | 57525.922 | 30326.585 | 70930.464 | 76753129.383 | 11912470.204 | 1720863.942 | 77158443.986 | -- | 0.773 | 0.873 | 0.953 | 1031.601 | 0.08 | 0.012 | 1037.048 | -- | 0.123 | 0.126 | 0.151 | 163.853 | -- | 1.169 | 1.32 | 1.441 | 1559.802 | 0.121 | 0.017 | -- | 1.643 | 30.304 | 0.696 | 1.173 | 1.698 | 28.721 | 0.723 | 1.221 | 2.827 | 3.279 | 0.031 | 1.432 | 2187.05 | 1941.71 | 993.882 | 1591.58 | -- | -- | 0.152 | 2.549 | 0.083 | 0.122 | 0.155 | 2.456 | 0.086 | 0.126 | 0.261 | 0.276 | 0.004 | 0.149 | 201.998 | 163.326 | 118.338 | 165.527 | -- | -- | 1.306 | 1.351 | 1.427 | 1584.585 | 0.116 | 0.017 | 1592.416 | -- | 39910787.024 | 2545675.754 | 53563210.132 | 0 | 6076326 | 1804394.784 | 43701387.15 | 612277 | 0 | 256087.291 | 333808 | 96609568.201 | 52194384.934 | 46118058.934 | 98413962.985 | 50389990.15 | 26.82% | 1.711% | 36% | 0% | 4.083% | 1.213% | 29.37% | 0.4115% | 0% | 0.1721% | 0.2243% | 64.92% | 35.08% | 30.99% | 66.14% | 33.86% |  | 6295.9048 | 9615.2289 | 9572.97 | 10827.0874 | 11888.5542 | 8398.6716 |  | 1109.4479
38 | 79 | SRMV - SERC Mississippi Valley |  | 47053.6 | 965440511.463 | 455888880.66 | 171263642.216 | 77991306.251 | 42061.647 | 20876.563 | 57893.46 | 66170856.618 | 6885060.388 | 958551.131 | 66399743.988 | -- | 0.491 | 0.535 | 0.676 | 772.737 | 0.04 | 0.006 | 775.41 | -- | 0.087 | 0.092 | 0.12 | 137.079 | -- | 0.671 | 0.732 | 0.924 | 1056.202 | 0.055 | 0.008 | -- | 1.465 | 0.676 | 0.53 | 0.674 | 1.48 | 0.673 | 0.567 | 0.732 | 4.501 | 10.106 | 0.007 | 0.922 | 2316.133 | 1356.568 | 857.053 | 1087.637 | -- | -- | 0.132 | 0.112 | 0.074 | 0.087 | 0.132 | 0.111 | 0.077 | 0.092 | 0.406 | 1.682 | 0.001 | 0.119 | 208.719 | 225.771 | 118.846 | 140.072 | -- | -- | 0.783 | 0.858 | 1.369 | 1177.033 | 0.066 | 0.009 | 1181.457 | -- | 19018042.17 | 1490088.07 | 100854647.672 | 42576416 | 2808987 | 1756556.435 | 0 | 578556 | 0 | 1981505.036 | 198843.45 | 166119542.398 | 5144099.435 | 2335112.435 | 125299682.833 | 45963959 | 11.1% | 0.8701% | 58.89% | 24.86% | 1.64% | 1.026% | 0% | 0.3378% | 0% | 1.157% | 0.1161% | 97% | 3.004% | 1.363% | 73.16% | 26.84% |  | 5637.1598 | 7764.8424 | 8403.057 | 11096.8958 | 6008.6016 | 7211.4585 |  | 1686.3275
39 | 78 | SRMW - SERC Midwest |  | 33434 | 884586277.127 | 404392121.103 | 114130603.651 | 49981762.231 | 65772.311 | 26710.534 | 151765.915 | 88053715.05 | 19525555.806 | 2830307.638 | 88719500.339 | -- | 1.153 | 1.069 | 2.66 | 1543.034 | 0.171 | 0.025 | 1554.701 | -- | 0.149 | 0.132 | 0.343 | 199.085 | -- | 1.46 | 1.354 | 3.369 | 1954.502 | 0.217 | 0.031 | -- | 1.57 | 26.393 | 0.772 | 1.462 | 1.398 | 32.497 | 0.789 | 1.309 | 3.913 | 6.325 | 0.009 | 3.374 | 2116.366 | 2449.438 | 950.658 | 1959.641 | -- | -- | 0.155 | 1.76 | 0.096 | 0.149 | 0.137 | 1.731 | 0.095 | 0.132 | 0.386 | 0.422 | 0.001 | 0.343 | 208.726 | 163.326 | 118.528 | 199.443 | -- | -- | 1.817 | 1.698 | 3.068 | 1763.198 | 0.179 | 0.026 | 1775.323 | -- | 76961284.9 | 109150.869 | 12561305.163 | 12641139 | 1943431 | 154275.012 | 9030729 | 411811 | 0 | 57622.285 | 259855.36 | 102590357.577 | 11540246.012 | 9596815.012 | 90103493.589 | 24027110 | 67.43% | 0.09564% | 11.01% | 11.08% | 1.703% | 0.1352% | 7.913% | 0.3608% | 0% | 0.05049% | 0.2277% | 89.89% | 10.11% | 8.409% | 78.95% | 21.05% |  | 7750.6492 | 9825.5692 | 8840.6111 | 10139.446 | 14997.2325 | 8020.5352 |  | 1350.5012
40 | 80 | SRSO - SERC South |  | 71735.6 | 1568926442.803 | 751613297.34 | 253393159.217 | 115281962.322 | 48724.933 | 21507.521 | 26817.758 | 113001503.285 | 17027149.805 | 2483958.163 | 113575839.927 | -- | 0.385 | 0.373 | 0.212 | 891.907 | 0.067 | 0.01 | 896.44 | -- | 0.062 | 0.057 | 0.034 | 144.049 | -- | 0.513 | 0.498 | 0.282 | 1189.807 | 0.09 | 0.013 | -- | 0.876 | 2.19 | 0.251 | 0.486 | 0.757 | 2.227 | 0.261 | 0.461 | 0.44 | 1.426 | 0.011 | 0.173 | 1910.395 | 1341.548 | 864.177 | 1254.871 | -- | -- | 0.088 | 0.331 | 0.034 | 0.058 | 0.074 | 0.328 | 0.035 | 0.054 | 0.044 | 0.216 | 0.002 | 0.021 | 190.945 | 202.899 | 118.034 | 150.813 | -- | -- | 0.769 | 0.652 | 0.389 | 1384.576 | 0.101 | 0.015 | 1391.437 | -- | 48764787.785 | 212953.727 | 130530117.076 | 48934913 | 8697476 | 10361945.552 | 0 | 5811458 | 0 | 78956.671 | 551.395 | 228522279.654 | 24870879.552 | 16173403.552 | 189949312.206 | 63443847 | 19.24% | 0.08404% | 51.51% | 19.31% | 3.432% | 4.089% | 0% | 2.293% | 0% | 0.03116% | 0.0002176% | 90.18% | 9.815% | 6.383% | 74.96% | 25.04% |  | 6191.6685 | 8320.7084 | 9180.747 | 10004.9491 | 6611.9005 | 7321.4243 |  | 1838.283
41 | 81 | SRTV - SERC Tennessee Valley |  | 56713.3 | 1157412925.789 | 548135000.224 | 214888097.399 | 97005398.603 | 43261.257 | 19633.451 | 63775.358 | 100093412.272 | 18610760.28 | 2688173.36 | 100724866.301 | -- | 0.403 | 0.405 | 0.594 | 931.586 | 0.087 | 0.013 | 937.463 | -- | 0.075 | 0.072 | 0.11 | 172.961 | -- | 0.686 | 0.69 | 1.012 | 1587.79 | 0.148 | 0.021 | -- | 1.086 | 57.599 | 0.183 | 0.686 | 1.042 | 58.587 | 0.168 | 0.663 | 1.785 | 5.206 | 0.006 | 0.995 | 2184.883 | 2944.354 | 878.076 | 1604.886 | -- | -- | 0.102 | 3.206 | 0.025 | 0.074 | 0.097 | 3.209 | 0.023 | 0.071 | 0.168 | 0.29 | 0.001 | 0.108 | 205.344 | 163.885 | 118.483 | 174.296 | -- | -- | 0.684 | 0.665 | 0.96 | 1636.169 | 0.151 | 0.022 | 1646.442 | -- | 67917640.842 | 161605.329 | 56268113.268 | 66383959 | 21694887 | 1655115.745 | 28186 | 702159 | 0 | 76403.401 | 28 | 190807749.84 | 24080347.745 | 2385460.745 | 126078906.585 | 88809191 | 31.61% | 0.0752% | 26.18% | 30.89% | 10.1% | 0.7702% | 0.01312% | 0.3268% | 0% | 0.03555% | 1.303e-05% | 88.79% | 11.21% | 1.11% | 58.67% | 41.33% |  | 5386.1193 | 9207.8189 | 9387.3009 | 10640.1112 | 17965.9761 | 7410.9872 |  | 1909.7626
42 | 82 | SRVC - SERC Virginia/Carolina |  | 95470 | 1475903823.218 | 690994324.883 | 323326028.744 | 144594057.91 | 48812.608 | 23552.479 | 30234.818 | 103410187 | 16875103.834 | 2374216.64 | 103925859.245 | -- | 0.302 | 0.326 | 0.187 | 639.665 | 0.052 | 0.007 | 642.855 | -- | 0.066 | 0.068 | 0.041 | 140.131 | -- | 0.557 | 0.601 | 0.345 | 1180.89 | 0.096 | 0.014 | -- | 1.272 | 9.105 | 0.182 | 0.51 | 1.278 | 5.327 | 0.176 | 0.53 | 0.824 | 4.457 | 0.024 | 0.264 | 1970.334 | 2119.284 | 911.861 | 1227.041 | -- | -- | 0.124 | 0.697 | 0.024 | 0.061 | 0.123 | 0.434 | 0.023 | 0.063 | 0.08 | 0.341 | 0.003 | 0.032 | 191.613 | 162.329 | 120.821 | 146.723 | -- | -- | 0.711 | 0.731 | 0.419 | 1356.968 | 0.116 | 0.016 | 1364.319 | -- | 43250487.271 | 601225.807 | 123030293.315 | 125460651 | 6109265 | 7399195.047 | 1434433 | 15182231.61 | 0 | 613120.662 | 245126 | 293200904.055 | 30125124.657 | 24015859.657 | 175139448.102 | 148186580.61 | 13.38% | 0.186% | 38.05% | 38.8% | 1.89% | 2.288% | 0.4436% | 4.696% | 0% | 0.1896% | 0.07581% | 90.68% | 9.317% | 7.428% | 54.17% | 45.83% |  | 4564.7541 | 8362.9765 | 9248.5023 | 10282.8827 | 13055.4861 | 7547.2062 |  | 2094.8861
43 | 89 | PRMS - Puerto Rico Miscellaneous |  | 6342.4 | 183865546.068 | 81019049.486 | 18578947.002 | 8256731.001 | 29903.264 | 12466.654 | 30510.252 | 14473222.329 | 1510125.003 | 239404.797 | 14527770.208 | -- | 3.219 | 3.02 | 3.284 | 1558.024 | 0.081 | 0.013 | 1563.896 | -- | 0.325 | 0.308 | 0.332 | 157.433 | -- | 3.303 | 3.098 | 3.37 | 1598.601 | 0.083 | 0.013 | -- | 2.504 | 4.431 | 2.218 | 3.302 | 2.519 | 4.064 | 2.163 | 3.1 | 2.721 | 5.901 | 0.355 | 3.369 | 2217.168 | 1690.614 | 1161.527 | 1598.384 | -- | -- | 0.233 | 0.428 | 0.232 | 0.325 | 0.233 | 0.397 | 0.226 | 0.308 | 0.253 | 0.57 | 0.037 | 0.332 | 205.912 | 163.232 | 121.373 | 157.433 | -- | -- | 3.831 | 3.575 | 4.455 | 1618.059 | 0.06 | 0.011 | 1622.693 | -- | 3257268 | 6908147.85 | 7944397.38 | 0 | 0 | 0 | 165727 | 305856.43 | 0 | 0 | -2449 | 18107364.23 | 471583.43 | 471583.43 | 18107364.23 | 471583.43 | 17.53% | 37.18% | 42.76% | 0% | 0% | 0% | 0.892% | 1.646% | 0% | 0% | 0% | 97.46% | 2.538% | 2.538% | 97.46% | 2.538% |  | 9896.446 | 10152.7888 | 10277.7626 | 10767.5512 | 10357.1236 | 9569.8961
44 | 53 | ASCC - Alaska Systems Coordinating Council | Alaska Systems Coordinating Council | 3043.8 | 42282342.817 | 16820174.223 | 6595817.773 | 2652125.527 | 20030.618 | 8286.973 | 1493.177 | 3034124.337 | 491825.784 | 68293.771 | 3050447.931 | -- | 6.074 | 6.249 | 0.453 | 920.015 | 0.075 | 0.01 | 924.964 | -- | 0.947 | 0.985 | 0.071 | 143.517 | -- | 8.39 | 8.633 | 0.625 | 1270.916 | 0.103 | 0.014 | -- | 1.907 | 17.671 | 7.33 | 8.422 | 1.779 | 17.917 | 8.147 | 8.779 | 0.938 | 2.406 | 0.027 | 0.625 | 2274.583 | 1469.902 | 976.325 | 1278.385 | -- | -- | 0.178 | 1.993 | 0.878 | 0.954 | 0.169 | 2.011 | 0.97 | 0.992 | 0.088 | 0.271 | 0.003 | 0.071 | 212.862 | 165.753 | 116.889 | 144.861 | -- | -- | 9.506 | 9.825 | 0.784 | 1278.374 | 0.112 | 0.016 | 1285.808 | -- | 752894.449 | 902485.641 | 3085396.015 | 0 | 1688900 | 38070.956 | 132212 | 0 | 0 | 0 | -4141 | 4736635.105 | 1859182.956 | 170282.956 | 4774706.061 | 1821112 | 11.41% | 13.67% | 46.75% | 0% | 25.59% | 0.5768% | 2.003% | 0% | 0% | 0% | 0% | 71.81% | 28.19% | 2.58% | 72.39% | 27.61% |  | 6410.4777 | 8824.908 | 8824.8321 | 10685.7166 | 8868.0265 | 8352.5824 |  | 1313.5593
45 | 54 | HICC - Hawaiian Islands Coordinating Council | Hawaiian Islands Coordinating Council | 3265.2 | 83268140.808 | 35217160.495 | 9180590.002 | 3973330.879 | 22256.984 | 9470.901 | 25333.243 | 6844000.054 | 1510077.131 | 230106.193 | 6897161.841 | -- | 4.849 | 4.767 | 5.519 | 1490.972 | 0.164 | 0.025 | 1502.553 | -- | 0.535 | 0.538 | 0.608 | 164.385 | -- | 5.767 | 5.67 | 6.564 | 1773.438 | 0.196 | 0.03 | -- | 2.825 | 6.286 | 0 | 5.76 | 2.779 | 6.249 | 0 | 5.715 | 5.228 | 7.245 | 0 | 6.939 | 2393.72 | 1652.646 | 0 | 1765.272 | -- | -- | 0.252 | 0.618 | 0 | 0.558 | 0.249 | 0.618 | 0 | 0.556 | 0.467 | 0.713 | 0 | 0.672 | 213.892 | 162.533 | 0 | 170.994 | -- | -- | 6.268 | 6.19 | 6.845 | 1748.41 | 0.173 | 0.027 | 1760.783 | -- | 1084555.1 | 6155207.42 | 0 | 0 | 114971 | 282637.444 | 657891 | 505994 | 183391 | 198724.533 | -2781 | 7435706.053 | 1744884.444 | 1629913.444 | 7718343.497 | 1462247 | 11.81% | 67.03% | 0% | 0% | 1.252% | 3.078% | 7.164% | 5.51% | 1.997% | 2.164% | 0% | 80.99% | 19.01% | 17.75% | 84.07% | 15.93% |  | 9070.0206 | 10323.5903 | 10224.9787 | 11191.2554 | 10168.0643 | - |  | 1798.2744
46 | 55 | MRO - Midwest Reliability Organization | Midwest Reliability Organization | 158253.2 | 2454245941.676 | 1224843041.474 | 459728134.663 | 204177921.354 | 161180.243 | 78836.618 | 178250.593 | 223671134.719 | 44406342.983 | 6407350.298 | 225178080.311 | -- | 0.701 | 0.772 | 0.775 | 973.058 | 0.097 | 0.014 | 979.614 | -- | 0.131 | 0.129 | 0.145 | 182.273 | -- | 1.29 | 1.421 | 1.427 | 1790.63 | 0.178 | 0.026 | -- | 1.499 | 7.038 | 0.731 | 1.274 | 1.488 | 4.766 | 0.733 | 1.259 | 2.058 | 1.702 | 0.027 | 1.426 | 2179.56 | 1486.487 | 1014.107 | 1815.747 | -- | -- | 0.143 | 0.721 | 0.086 | 0.129 | 0.142 | 0.583 | 0.084 | 0.127 | 0.197 | 0.174 | 0.003 | 0.145 | 208.326 | 152.225 | 118.901 | 184.156 | -- | -- | 1.334 | 1.307 | 1.306 | 1716.515 | 0.159 | 0.023 | 1727.21 | -- | 162116978.557 | 1053037.362 | 82434806.958 | 29578125 | 17200563.42 | 3255892.368 | 159882565.15 | 3242909.21 | 0 | 574162.098 | 389096.609 | 276146206.584 | 183581930.148 | 166381366.728 | 249823973.952 | 209904162.78 | 35.26% | 0.2291% | 17.93% | 6.434% | 3.741% | 0.7082% | 34.78% | 0.7054% | 0% | 0.1249% | 0.08464% | 60.07% | 39.93% | 36.19% | 54.34% | 45.66% |  | 5338.4724 | 9859.8308 | 9320.9833 | 10462.2563 | 9765.0649 | 8529.0031 |  | 2016.1261
47 | 56 | NPCC - Northeast Power Coordinating Council | Northeast Power Coordinating Council | 83910.6 | 996720175.682 | 478226701.578 | 226868281.265 | 100704848.132 | 30355.619 | 14013.866 | 7191.068 | 55982730.068 | 10811599.145 | 1387291.939 | 56324564.996 | -- | 0.268 | 0.278 | 0.063 | 493.526 | 0.048 | 0.006 | 496.54 | -- | 0.061 | 0.059 | 0.014 | 112.334 | -- | 0.494 | 0.514 | 0.117 | 910.883 | 0.088 | 0.011 | -- | 2.535 | 3.738 | 0.259 | 0.285 | 3.68 | 3.598 | 0.265 | 0.291 | 1.387 | 1.287 | 0.036 | 0.047 | 2293.733 | 1465.074 | 895.312 | 902.296 | -- | -- | 0.227 | 0.337 | 0.034 | 0.038 | 0.271 | 0.271 | 0.035 | 0.038 | 0.124 | 0.116 | 0.005 | 0.006 | 204.931 | 132.252 | 119.372 | 119.808 | -- | -- | 0.461 | 0.446 | 0.115 | 955.251 | 0.053 | 0.007 | 958.582 | -- | 578806.817 | 923965.097 | 111405843.722 | 58249209 | 34214584.56 | 7231929.638 | 7936528.25 | 3548290.32 | 0 | 2696426.225 | 82696 | 173936946.861 | 52931332.768 | 18716748.208 | 122919667.499 | 103948612.13 | 0.2551% | 0.4073% | 49.11% | 25.68% | 15.08% | 3.188% | 3.498% | 1.564% | 0% | 1.189% | 0.03645% | 76.67% | 23.33% | 8.25% | 54.18% | 45.82% |  | 4393.3871 | 7531.1832 | 7973.1821 | 11192.7088 | 11077.8967 | 7500.1843 |  | 1047.5062
48 | 57 | RFC - Reliability First Corporation | Reliability First Corporation | 251144.5 | 5323074878.312 | 2485580177.009 | 917396151.218 | 405878511.783 | 229856.253 | 96395.743 | 282779.778 | 436865019.311 | 76468264.46 | 10829875.087 | 439433058.265 | -- | 0.501 | 0.475 | 0.616 | 952.402 | 0.083 | 0.012 | 958.001 | -- | 0.086 | 0.078 | 0.106 | 164.14 | -- | 0.767 | 0.727 | 0.943 | 1457.125 | 0.128 | 0.018 | -- | 1.257 | 3.623 | 0.285 | 0.737 | 1.081 | 3.19 | 0.291 | 0.677 | 2.058 | 2.34 | 0.02 | 0.947 | 2179.514 | 2123.441 | 878.208 | 1472.173 | -- | -- | 0.119 | 0.285 | 0.039 | 0.083 | 0.102 | 0.252 | 0.039 | 0.075 | 0.195 | 0.184 | 0.003 | 0.107 | 206.564 | 167.048 | 118.987 | 166.787 | -- | -- | 0.997 | 0.912 | 1.165 | 1671.178 | 0.154 | 0.022 | 1681.563 | -- | 257895950.878 | 2922904.882 | 324008780.377 | 269475516 | 8132630.12 | 7062971.808 | 35143808.83 | 5018281.4 | 0 | 7315209.359 | 420096.946 | 862038458.442 | 55357692.158 | 47225062.038 | 599625914.25 | 317770236.35 | 28.11% | 0.3186% | 35.32% | 29.37% | 0.8865% | 0.7699% | 3.831% | 0.547% | 0% | 0.7974% | 0.04579% | 93.97% | 6.034% | 5.148% | 65.36% | 34.64% |  | 5802.3732 | 8826.6651 | 10019.8337 | 10551.2771 | 12711.5619 | 7380.7055 |  | 1689.2517
49 | 58 | SERC - Southeastern Electric Reliability Corporation | SERC Reliability Corporation | 377907.8 | 7723086390.74 | 3660597828.17 | 1330175374.62 | 606136780.901 | 291015.919 | 132382.98 | 364530.98 | 579337487.471 | 91862976.496 | 13055470.933 | 582371684.21 | -- | 0.438 | 0.437 | 0.548 | 871.069 | 0.069 | 0.01 | 875.631 | -- | 0.075 | 0.072 | 0.094 | 150.027 | -- | 0.631 | 0.63 | 0.79 | 1255.456 | 0.1 | 0.014 | -- | 1.169 | 1.163 | 0.278 | 0.601 | 1.093 | 1.102 | 0.281 | 0.585 | 1.983 | 9.495 | 0.023 | 0.761 | 2026.045 | 1383.677 | 875.981 | 1291.41 | -- | -- | 0.114 | 0.185 | 0.038 | 0.072 | 0.106 | 0.171 | 0.038 | 0.069 | 0.194 | 1.509 | 0.003 | 0.091 | 197.979 | 219.932 | 119.432 | 154.283 | -- | -- | 0.716 | 0.7 | 0.767 | 1315.759 | 0.098 | 0.014 | 1322.252 | -- | 274583838.963 | 6159992.918 | 609669351.51 | 324055365 | 42762443 | 25928617.909 | 9695370 | 30750530.61 | 0 | 4467857.985 | 2102006.058 | 1221038412.434 | 109136961.519 | 66374518.519 | 922911665.343 | 407263708.61 | 20.64% | 0.4631% | 45.83% | 24.36% | 3.215% | 1.949% | 0.7289% | 2.312% | 0% | 0.3359% | 0.158% | 91.8% | 8.205% | 4.99% | 69.38% | 30.62% |  | 5806.0663 | 8370.3973 | 8528.2176 | 10233.6359 | 6291.3855 | 7334.5586 |  | 1503.8852
50 | 59 | TRE - Texas Regional Entity | Texas Regional Entity | 129179.3 | 2246299808.856 | 1149333330.337 | 418341926.945 | 198234572.783 | 99120.523 | 47249.92 | 123706.072 | 170374347.313 | 22885945.162 | 3190835.823 | 171135856.167 | -- | 0.474 | 0.477 | 0.591 | 814.522 | 0.055 | 0.008 | 818.163 | -- | 0.088 | 0.082 | 0.11 | 151.693 | -- | 0.731 | 0.735 | 0.912 | 1255.937 | 0.084 | 0.012 | -- | 1.109 | 3.909 | 0.59 | 0.731 | 1.083 | 3.874 | 0.539 | 0.683 | 3.172 | 9.809 | 0.007 | 0.912 | 2256.778 | 2155.877 | 869.744 | 1259.987 | -- | -- | 0.103 | 0.313 | 0.08 | 0.088 | 0.101 | 0.309 | 0.073 | 0.082 | 0.295 | 0.785 | 0.001 | 0.11 | 210.069 | 172.563 | 118.44 | 152.242 | -- | -- | 0.781 | 0.709 | 0.74 | 1182.164 | 0.065 | 0.009 | 1186.451 | -- | 74510144.05 | 261481.947 | 193547724.376 | 40211257 | 684520.26 | 773485.116 | 91538791.55 | 14597105 | 0 | 1799765.717 | 417652 | 310748025.09 | 107593901.926 | 106909381.666 | 271310253.206 | 147031673.81 | 17.81% | 0.0625% | 46.27% | 9.612% | 0.1636% | 0.1849% | 21.88% | 3.489% | 0% | 0.4302% | 0.09984% | 74.28% | 25.72% | 25.56% | 64.85% | 35.15% |  | 5369.5307 | 8276.2116 | 7765.032 | 10743.0321 | 12493.2749 | 7343.33 |  | 1360.5563
51 | 60 | WECC - Western Electricity Coordinating Council | Western Electricity Coordinating Council | 245239.2 | 3489665444.242 | 1648558715.954 | 733279395.87 | 336109835.866 | 196888.369 | 90825.227 | 80695.576 | 265218156.13 | 41677200.595 | 5827401.029 | 266601858.825 | -- | 0.537 | 0.54 | 0.22 | 723.375 | 0.057 | 0.008 | 727.149 | -- | 0.113 | 0.11 | 0.046 | 152.002 | -- | 1.012 | 1.018 | 0.415 | 1363.205 | 0.107 | 0.015 | -- | 1.713 | 4.012 | 0.592 | 0.977 | 1.721 | 3.721 | 0.579 | 0.955 | 1.131 | 15.286 | 0.008 | 0.41 | 2292.854 | 1817.031 | 926.242 | 1390.681 | -- | -- | 0.155 | 0.477 | 0.076 | 0.11 | 0.156 | 0.45 | 0.074 | 0.107 | 0.102 | 1.817 | 0.001 | 0.046 | 206.848 | 215.951 | 118.578 | 155.877 | -- | -- | 0.961 | 0.914 | 0.323 | 1324.397 | 0.09 | 0.012 | 1330.361 | -- | 125855927.848 | 779957.008 | 250456892.55 | 56618516 | 141630439.4 | 8966845.985 | 73113896.41 | 57015395.02 | 15791376 | 2263001.937 | 787146.544 | 436761441.887 | 296517952.815 | 154887513.415 | 389109771.872 | 344169622.83 | 17.16% | 0.1064% | 34.16% | 7.721% | 19.31% | 1.223% | 9.971% | 7.775% | 2.154% | 0.3086% | 0.1073% | 59.56% | 40.44% | 21.12% | 53.06% | 46.94% |  | 4758.9847 | 8921.6562 | 8496.4235 | 11084.7289 | 8414.0893 | 7811.2466 |  | 1493.1401
52 | 61 | PR - Puerto Rico | Puerto Rico | 6342.4 | 183865546.068 | 81019049.486 | 18578947.002 | 8256731.001 | 29903.264 | 12466.654 | 30510.252 | 14473222.329 | 1510125.003 | 239404.797 | 14527770.208 | -- | 3.219 | 3.02 | 3.284 | 1558.024 | 0.081 | 0.013 | 1563.896 | -- | 0.325 | 0.308 | 0.332 | 157.433 | -- | 3.303 | 3.098 | 3.37 | 1598.601 | 0.083 | 0.013 | -- | 2.504 | 4.431 | 2.218 | 3.302 | 2.519 | 4.064 | 2.163 | 3.1 | 2.721 | 5.901 | 0.355 | 3.369 | 2217.168 | 1690.614 | 1161.527 | 1598.384 | -- | -- | 0.233 | 0.428 | 0.232 | 0.325 | 0.233 | 0.397 | 0.226 | 0.308 | 0.253 | 0.57 | 0.037 | 0.332 | 205.912 | 163.232 | 121.373 | 157.433 | -- | -- | 3.831 | 3.575 | 4.455 | 1618.059 | 0.06 | 0.011 | 1622.693 | -- | 3257268 | 6908147.85 | 7944397.38 | 0 | 0 | 0 | 165727 | 305856.43 | 0 | 0 | -2449 | 18107364.23 | 471583.43 | 471583.43 | 18107364.23 | 471583.43 | 17.53% | 37.18% | 42.75% | 0% | 0% | 0% | 0.8919% | 1.646% | 0% | 0% | 0% | 97.46% | 2.538% | 2.538% | 97.46% | 2.538% |  | 9896.446 | 10152.7888 | 10277.7626 | 10767.5512 | 10357.1236 | 9569.8961 |  | 1198.7851
SEQST00 tate sequence number |  | AVERT Region |  | Avoided CO2 Rate (lb/MWh) | Avoided NOx Rate (lb/MWh) | Avoided SO2 Rate (lb/MWh) | Avoided PM2.5 Rate (lb/MWh) | Avoided CH4 (lb/MWh) | Avoided N2O (lb/MWh) | Calculated eGRID Annual Heat Rate (Btu/kWh) |  | Heat Rate Calculation for AVERT Region with multiple eGRID Subregions |  |  | eGRID Region 1 % | eGRID Region 2 % | eGRID Region 3 %
1 |  | AVERT - National Average |  | 1438 | 0.7 | 0.67 | 0.08 | 0.085 | 0.012 | 8934 |  | US Average | - | - | - | - | -
2 |  | AVERT - California |  | 1069 | 0.28 | 0.05 | 0.05 | 0.031 | 0.01 | 7926.8297 |  | CAMX - WECC California | - | - | - | - | -
3 |  | AVERT - Carolinas |  | 1434 | 0.67 | 0.41 | 0.12 | 0.052 | 0.007 | 8362.9765 |  | SRVC - SERC Virginia/Carolina | - | - | - | - | -
4 |  | AVERT - Central |  | 1823 | 1.27 | 1.39 | 0.08 | 0.089247 | 0.013321 | 9765.1478 |  | SPNO - SPP North | SPSO - SPP South | - | 33.02% | 66.98% | -
5 |  | AVERT - Florida |  | 1069 | 0.32 | 0.21 | 0.07 | 0.053 | 0.007 | 7513.7594 |  | FRCC - FRCC All | - | - | - | - | -
6 |  | AVERT - Mid-Atlantic |  | 1482 | 0.63 | 0.79 | 0.09 | 0.078545 | 0.011496 | 7817.256 |  | RFCE - RFC East | RFCW - RFC West | - | 35.77% | 64.23%
7 |  | AVERT - Midwest |  | 1677 | 1 | 1.27 | 0.1 | 0.099105 | 0.014243 | 9252.1981 |  | SRMW - SERC Midwest | MROW - MRO West | SRMV - SERC Mississippi Valley | 21.61% | 45.97% | 32.42%
8 |  | AVERT - New England |  | 1110 | 0.25 | 0.22 | 0.04 | 0.072 | 0.009 | 7143.6262 |  | NEWE - NPCC New England | - | - | - | - | -
9 |  | AVERT - New York |  | 1110 | 0.47 | 0.24 | 0.14 | 0.026198 | 0.0032862 | 7489.2205 |  | NYUP - NPCC Upstate NY | NYLI - NPCC Long Island | NYCW - NPCC NYC/Westchester | 65.8% | 9.187% | 25.01%
10 |  | AVERT - Northwest |  | 1480 | 0.78 | 0.42 | 0.09 | 0.058 | 0.008 | 9252.7754 |  | NWPP - WECC Northwest | - | - | - | - | -
11 |  | AVERT - Rocky Mountains |  | 1890 | 0.92 | 0.61 | 0.03 | 0.109 | 0.016 | 10228.497 |  | RMPA - WECC Rockies | - | - | - | - | -
12 |  | AVERT - Southeast |  | 1369 | 0.68 | 0.17 | 0.06 | 0.067 | 0.01 | 8320.7084 |  | SRSO - SERC South | - | - | - | - | -
13 |  | AVERT - Southwest |  | 1332 | 0.47 | 0.22 | 0.08 | 0.052 | 0.007 | 8729.4035 |  | AZNM - WECC Southwest | - | - | - | - | -
14 |  | AVERT - Tennessee |  | 1372 | 0.47 | 0.57 | 0.12 | 0.087 | 0.013 | 9207.8189 |  | SRTV - SERC Tennessee Valley | - | - | - | - | -
15 |  | AVERT - Texas |  | 1207 | 0.55 | 0.42 | 0.06 | 0.054 | 0.008 | 8267.9012 |  | ERCT - ERCOT All | - | - | - | - | -
Note on K46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Manuall paste these values in - something always gets messed up with the lookup
Note on I47: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: All of these cells calculated by weighted averages from percentages at right (eGRID matched regions)

## Profiles (hidden)
Displaced Electricity | 1 | AVERT Uniform EE Factors (2022 Data)
| AVERT - National Average | NERC/AVERT Region
| NOx | 0.7 | lb/MWh Average |  | CH4 | 0.085 | lb/MWh Average
| SO2 | 0.67 | lb/MWh Average |  | N2O | 0.012 | lb/MWh Average
| CO2 | 1438 | lb/MWh Average
| Heat Rate | 8934 | Btu/kWh Average
Generation Sources
Name | Code | Btu/kWh | NOx lb/MMBtu | SO2 lb/MMBtu | CO2 lb/MMBtu |  | NOx lb/MWh | SO2 lb/MWh | CO2 lb/MWh | CH4 lb/MWh | N2O lb/MWh
AVERT Uniform EE | 1 | 8934 | - | - | - |  | 0.7 | 0.67 | 1438 | 0.085 | 0.012
EGrid Annual Average | 2 | n/a | #N/A | #N/A | #N/A |  | n/a | n/a | n/a | #N/A | #N/A
EGrid Annual Fossil | 3 | n/a | #N/A | #N/A | #N/A |  | n/a | n/a | n/a | #N/A | #N/A
EGrid Annual Non-Baseload | 4 | n/a | - | - | - |  | n/a | n/a | n/a | #N/A | #N/A
EGrid Annual Coal | 5 | n/a | #N/A | #N/A | #N/A |  | n/a | n/a | n/a | #VALUE! | #VALUE!
EGrid Annual Oil | 6 | n/a | #N/A | #N/A | #N/A |  | n/a | n/a | n/a | #VALUE! | #VALUE!
EGrid Annual Natural Gas | 7 | n/a | #N/A | #N/A | #N/A |  | n/a | n/a | n/a | #VALUE! | #VALUE!
Coal Boiler 3.8 lb/MWh NOx | 8 | 9500 | 0.4 | 0.52632 | 207.1 |  | 3.8 | 5 | 1967.45 | 0.23032 | 0.033501 | 36
Coal Boiler 1.5 lb/MWh NOx | 9 | 9500 | 0.15789 | 0.26316 | 207.1 |  | 1.5 | 2.5 | 1967.45 | 0.23032 | 0.033501
Coal Boiler with SCR 0.8 lb/MWh NOx | 10 | 9500 | 0.084211 | 0.10526 | 207.1 |  | 0.8 | 1 | 1967.45 | 0.23032 | 0.033501
Gas Boiler 0.77 lb/MWh NOx | 11 | 11000 | 0.07 | 0.00056699 | 116.9 |  | 0.77 | 0.0062369 | 1285.9 | 0.024244 | 0.0024244
Gas Turbine Peaker 25 ppm | 12 | 12000 | 0.091912 | 0.00056699 | 116.9 |  | 1.1029 | 0.0068039 | 1402.8 | 0.026448 | 0.0026448
Gas combined-cycle 9 ppm | 13 | 8000 | 0.033088 | 0.00056699 | 116.9 |  | 0.26471 | 0.0045359 | 935.2 | 0.017632 | 0.0017632
Gas combined-cycle 3 ppm | 14 | 7000 | 0.011029 | 0.00056699 | 116.9 |  | 0.077206 | 0.0039689 | 818.3 | 0.015428 | 0.0015428
User Source 1 | 15 | 0 |  |  |  |  | 0 | 0 | 0
User Source 2 | 16 | 0 |  |  |  |  | 0 | 0 | 0
User Source 3 | 17 | 0 |  |  |  |  | 0 | 0 | 0

## Factors (hidden)
Factors
General Emission Factors
3.11 |  | gm/hp-hr to lb/MWh for recip engines
0.27273 |  | ratio of carbon to CO2
0.90662 |  | ratio of tonnes to tons | 7.27
8.67 |  | metric tons of Carbon per home | 1.9827
4.63 |  | metric tons of Carbon per car
12000 |  | Btu per ton of cooling capacity
12183 |  | kWh per average U.S. home per year
0.0034121 |  | MMBtu/kWh
525.2778 |  | gal/vehicle
0.1204 |  | MMBtu/gal (gasoline)
Oil
138000 |  | Btu/gallon distillate oil
304 |  | lb/bbl distillate oil
7.2381 | lb/gal | distillate oil
150000 |  | Btu/gallon residual oil
331 |  | lb/bbl residual oil
163.1 |  | lb/MMBtu CO2 emission factor
235 |  | ppm per lb/MMBtu LHV for diesel @15%O2
258 |  | ppm per lb/MMBtu HHV for diesel @15%O2
780 |  | ppm per lb/MMBtu HHV for diesel @3%O2
0.0005 | % | Lower limit of sulfur content
0.05 | % | Upper limit of sulfur content
5 | ppm | Lower limit of sulfur content
5000 | ppm | Upper limit of sulfur content
20000 | Btu/lb | Heat content of oil (distillate
0.006612 |  | lb/MMBtu CH4 emission factor
0.0013224 |  | lb/MMBtu N20 emission factor
Natural Gas
0.4238 |  | lb/cf heat content of natural gas
1028 |  | Btu/cf of natural gas
7.097e-05% |  | sulfur content of natural gas
116.9 |  | lb/MMBtu CO2 emission factor
247.52 |  | ppm per lb/MMBtu LHV for natural gas @15%O2
272 |  | ppm per lb/MMBtu HHV for natural gas @15%O2
823 |  | ppm per lb/MMBtu HHV for natural gas @3%O2
0.002204 |  | lb/MMBtu CH4 emission factor
0.0002204 |  | lb/MMBtu N20 emission factor
Propane
91600 |  | Btu/gallon
139 |  | lb/MMBtu CO2 emission factor
7.097e-05% |  | sulfur content of natural gas
582 |  | kg/m3
4.2 |  | lb/gal
0.002204 |  | lb/MMBtu CH4 emission factor
0.0002204 |  | lb/MMBtu N20 emission factor
Coal
21.015 |  | MMBtu/ton
207.1 |  | lb/MMBtu CO2 emission factor
11175 | Btu/lb
0.024244 |  | lb/MMBtu CH4 emission factor
0.0035264 |  | lb/MMBtu N20 emission factor
Woody Biomass
206.7 |  | lb/MMBtu CO2 emission factor
7500 |  | Btu/lb
0.07 |  | lb/MMBtu CH4 emission factor
0.009 |  | lb/MMBtu N20 emission factor
CHP Technologies
100% |  | Accept kW capacity values that are THIS percent of the lowest sample
100% |  | Accept kW capacity values that are THIS percent of the highest sample
0.07 | % | Minimum efficiency of CHP
0.66 | % | Maximum efficiency of CHP
5169.697 | Btu/kWh HHV | Minimum HHV of CHP
48742.8571 | Btu/kWh HHV | Maximum HHV of CHP
4704.4242 | Btu/kWh LHV | Minimum LHV of CHP
44356 | Btu/kWh LHV | Maximum LHV of CHP
0.05 |  | Minimum Power to Heat ratio for CHP
10 |  | Maximum Power to Heat ratio for CHP
1 | ppm | Minimum NOx rate for CHP
200 | ppm | Maximum NOx rate for CHP
0.05 | gm/hphr | Minimum NOx rate for CHP
20 | gm/hphr | Maximum NOx rate for CHP
0.005 | lb/MMBtu | Minimum NOx rate for CHP
0.8 | lb/MMBtu | Maximum NOx rate for CHP
0.05 | lb/MMBtu | Minimum NOx rate for CHP
8 | lb/MMBtu | Maximum NOx rate for CHP
Thermal Production
66% |  | Minimum efficiecy of thermal production technology
99% |  | Maximum efficiecy of thermal production technology
350% |  | Maximum efficiecy of electric technology
1100 |  | btu/lb steam
Active Cell Highlighting
Cell to Highlight
Global Warming Potential
CO2 | 1
CH4 | 21
N2O | 310
Fuel and Technology Match
1
tech
0 | #N/A | #N/A
1 | 1 | 7
2 | 1 | 7
3 | 1 | 7
4 | 1 | 7
5 | 1 | 7
6 | 1 | 7
7 | 1 | 7
8 | 1 | 7
9 | 8 | 8
10 | 8 | 8

## Calc1 (hidden)
Calculations
Total Emissions | CHP | Displaced Generation - Total | Displaced Thermal Supply - Total
Number of CHP Units: | 1
Generating Capacity (kW) | 0
CHP Generation (MWh/year) | 0
CHP fuel consumption (MMBtu/year) | 0 | 0 | 0
Duct Burner fuel (MMBtu/year) | 0
CHP with Duct Burners
NOx (tons/year) | 0 | 0 | 0
SO2 (tons/year) | #DIV/0! | 0 | 0
CO2 (tons/year) | #DIV/0! | 0 | 0
CHP Unit
NOx (tons/year) | 0 | 0 | 0 | CH4 (tons/year) | #N/A
SO2 (tons/year) | 0 | 0 | 0 | N2O (tons/year) | #N/A
CO2 (tons/year) | 0 | 0 | 0
Duct Burners
NOx (tons/year) | 0 |  |  | CH4 (tons/year) | 0
SO2 (tons/year) | #DIV/0! |  |  | N2O (tons/year) | 0
CO2 (tons/year) | #DIV/0!
| CHP | Displaced Generation per CHP unit | Displaced Thermal Supply per CHP unit
Unit Emissions for CHP System
Generating Capacity (kW) | 0
CHP Generation (MWh/year) | 0
CHP fuel consumption (MMBtu/year) | 0 | 0 | 0
Duct Burner fuel (MMBtu/year) | 0
CHP with Duct Burners
NOx (tons/year) | 0 | 0 | 0 | CH4 (tons/year) | #N/A
SO2 (tons/year) | #DIV/0! | 0 | 0 | N2O (tons/year) | #N/A
CO2 (tons/year) | #DIV/0! | 0 | 0
CHP Unit
NOx (tons/year) | 0 | 0 | 0 | CH4 (tons/year) | #N/A
SO2 (tons/year) | 0 | 0 | 0 | N2O (tons/year) | #N/A
CO2 (tons/year) | 0 | 0 | 0
Duct Burners
NOx (tons/year) | 0 |  |  | CH4 (tons/year) | 0
SO2 (tons/year) | #DIV/0! |  |  | N2O (tons/year) | 0
CO2 (tons/year) | #DIV/0!
CHP Technology | 0 | #N/A
Capacity | 0 | kW
Hours | 0 | hours
Percent of hours | 0%
Calc Hours
CHP Fuel Input (rounded) | 0 | MMBtu/hr
CHP Fuel | 0 | #N/A
CHP operating profile | #N/A
Max CHP Gen | 0 | MWh/yr
CHP Gen | 0 | MWh/yr
| 0 | MMBtu/yr elec gen equiv
CHP eff input % | 0%
CHP eff input Btu/kWh HHV | 0
CHP eff input Btu/kWh LHV | 0
CHP Fuel HHV-LHV | 0.91085
CHP HHV | FALSE | Btu/kWh
CHP percent | #DIV/0!
CHP Fuel input Btu | 0 | MMBtu/year
CHP NOx input ppm | 0 | ppm
CHP NOx input gm/hp-hr | 0 | gm/hp-hr
CHP NOx input lb/MMBtu | 0 | lb/MMBtu
CHP NOx input lb/MWh | 0 | lb/MWh
CHP NOxconv | 258
CHP NOxrate Btu | #DIV/0! | lb/MMBtu
CHP NOxrate | #DIV/0! | lb/MWh
CHP NOx | 0 | tons/year
CHP sulfur % | 0%
CHP sulfur input ppm | 0 | ppm
Calculated sulfur % | 0
CHP Fuel heat content | 0 | 0
Adj CHP Fuel Heat content | 0 | Btu/lb
CHP massfuel | 0 | tons/year
CHP SO2 | 0 | tons/year
CHP SO2 rate | #DIV/0! | lb/MWh | CHP CH4 | #N/A | tons/year
|  |  | CHP N2O | #N/A | tons/year
CHP CO2 | 0 | tons/year
CHP CO2 Rate | #DIV/0! | lb/MWh
Steam Turbine
Steam Consumption lb Steam/hr | 0
Steam Consumption MMBtu Steam/hr | 0
Calc Steam Cons MMBtu/hr | 0
Boiler Efficiency | 0%
B/ST Fuel Consumption MMBtu/yr | 0
B/ST Steam Displaced MMBtu/yr | 0
Duct Burners
Capacity of Duct Burners | 0 | MMBtu/hr
Duct Burner Hours | 0 | hours/year
Duct Burner Btu | 0 | MMBtu/year
Duct Burner NOx rate | 0 | lb/MMBtu
Duct Burner SO2 rate | #DIV/0! | lb/MMBtu | Duct Burner CH4 rate | 0.002204 | lb/MMBtu
Duct Burner CO2 rate | #DIV/0! | lb/MMBtu | Duct Burner N2O rate | 0.0002204 | lb/MMBtu
Duct Burner NOx | 0 | tons/year | Duct Burner CH4 | 0 | tons/year
Duct Burner SO2 | #DIV/0! | tons/year | Duct Burner N2O | 0 | tons/year
Duct Burner CO2 | #DIV/0! | tons/year
Cooling
Chiller | 0 | #N/A
Cooling Hours | 0 | Hours/year
Available Thermal | 0 | MMBtu/hr
Available based on user data (not rounded) | 0 | tons of cooling
Available based on user data | 0 | tons of cooling
Available based on user data (not rounded) | 0 | MMBtu/hr of cooling
Available based on user data | 0 | MMBtu/hr of cooling
CHP Cooling COP | 0 | COP
Cooling | 0 | MMBtu/hr
Thermal Demand for cooling | 0 | MMBtu/hr
Thermal Demand for cooling | 0 | MMBtu/year
Excess Thermal | 0 | MMBtu/year
Lost Simultaneous Heating | 0 | MMBtu/year
Off season heating | 0 | MMBtu/year
Displaced Cooling Technology | 0 | #N/A
Displaced Cooling COP | 0 | COP
Displaced Cooling Elec Demand | 0 | MMBtu/hr
Displaced Cooling Elec Demand | 0 | MWh/hr
Displaced Cooling Elec Demand | 0 | MWh/year
Displaced Generation
DE method input | 1 | AVERT Uniform EE Factors (2022 Data)
EGrid State | 1 | AVERT - National Average
DE NOx rate | 0.7 | lb/MWh | DE CH4 rate | 0.085 | lb/MWh
DE SO2 rate | 0.67 | lb/MWh | DE N2O rate | 0.012 | lb/MWh
DE CO2 rate | 1438 | lb/MWh
DE Heat Rate | 8934 | Btu/kWh
Displaced Generation (CHP) | 0 | MWh/year per CHP unit
Displaced Generation (Cooling) | 0 | MWh/year per CHP unit
Displaced Generation (heating) | 0 | MWh/year per CHP unit
Transmission Losses | 0%
Transmission Losses | 0 | MWh/year per CHP unit
Total Displaced Generating - Calc | 0 | MWh/year per CHP unit
Total Displaced Generating - Manual | 0 | MWh/year (estimated by user)
DE NOx | 0 | tons/year per CHP unit | DE CH4 | 0 | tons/year per CHP unit
DE SO2 | 0 | tons/year per CHP unit | DE N2O | 0 | tons/year per CHP unit
DE CO2 | 0 | tons/year per CHP unit
DE MMBtu | 0 | MMBtu/year per CHP unit
Displaced Thermal Supply
Thermal Utilization % | 0%
Power to Heat ratio | 0
Heat from CHP units | 0 | MMBtu/yr
Heat from Duct Burners | 0 | MMBtu/yr
Heat from CHP units to cooling | 0 | MMBtu/yr
Heat from CHP units "lost" | 0 | MMBtu/yr
Heat from CHP units to thermal use | 0 | MMBtu/yr
Heat from WHP to thermal use | FALSE | MMBtu/yr | 0
Stm source input | 0
Stm sulfur input % | 0%
Stm sulfur input ppm | 0
Calculated Stm sulfur % | 0%
Stm Efficiency | 0%
Stm BoilFuel | 0 | MMBtu/year
Max Stm BoilFuel | #DIV/0! | MMBtu/year
STM Fuel heat content | 0
Adj STM Fuel Heat content | 0 | Btu/lb
Stm boil fuel mass | 0 | tons/year
Stm SO2 | 0 | tons/year
Stm NOx rate | 0 | lb/MMBtu | Stm CH4 rate | 0 | lb/MMBtu
Stm NOx | 0 | tons/year | Stm CH4 | 0 | tons/year
Stm CO2 rate | 0 | lb/MMBtu | Stm N2O rate | 0 | lb/MMBtu
Stm Co2 | 0 | tons/year | Stm N2O | 0 | tons/year
Displaced Heating Electricity
Heat from CHP units to thermal use | 0 | MMBtu/year
Electric Efficiency of Heating Unit | 0
| 0 | MMBtu/hr
Displaced Heating Elec Demand | 0 | MWh/hr
Displaced Heating Elec Demand | 0 | MWh/year
Note on B107: Anne Hampson: The 0.88 is the assumed efficiency of the duct burner